## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-01-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.45 |  | 0.45
2 |  |  |  |  | 0.39 |  | 0.39
3 |  |  |  |  | 0.44 |  | 0.44
4 |  |  |  |  | 0.39 |  | 0.39
5 |  |  |  |  | 0.37 |  | 0.37
6 |  |  |  |  | 0.48 |  | 0.48
7 |  |  |  |  | 0.35 |  | 0.35
8 |  |  |  |  | 0.34 |  | 0.34
9 |  |  |  |  | 0.45 |  | 0.45
10 |  |  |  |  | 0.42 |  | 0.42
11 |  |  |  |  | 0.38 |  | 0.38
12 |  |  |  |  | 0.37 |  | 0.37
13 |  |  |  |  | 0.31 |  | 0.31
14 |  |  |  |  | 0.36 |  | 0.36
15 |  |  |  |  | 0.44 |  | 0.44
16 |  |  |  |  | 0.23 |  | 0.23
17 |  |  |  |  | 0.26 |  | 0.26
18 |  |  |  |  | 0.28 |  | 0.28
19 |  |  |  |  | 0.28 |  | 0.28
20 |  |  |  |  | 0.28 |  | 0.28
21 |  |  |  |  | 0.22 |  | 0.22
22 |  |  |  |  | 0.22 |  | 0.22
23 |  |  |  |  | 0.24 |  | 0.24
24 |  |  |  |  | 0.45 |  | 0.45
25 |  |  |  |  | 0.27 |  | 0.27
26 |  |  |  |  | 0.2 |  | 0.2
27 |  |  |  |  | 0.18 |  | 0.18
28 |  |  |  |  | 0.2 |  | 0.2
29 |  |  |  |  | 0.19 |  | 0.19
30 |  |  |  |  | 0.18 |  | 0.18
31 |  |  |  |  | 0.19 |  | 0.19
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 2/04/2025
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 3 | 50 | 150 | 5.6 | 7.3 | 72.5862 | yes | 7
2 | 2.5 | 50 | 125 | 6.1 | 7.4 | 68.5994 | yes | 7
3 | 2.8 | 50 | 140 | 8.9 | 7.2 | 54.6291 | yes | 7
4 | 2.8 | 50 | 140 | 8.6 | 7.3 | 57.788 | yes | 7
5 | 2.7 | 50 | 135 | 9 | 7.3 | 55.6008 | yes | 7
6 | 3.1 | 50 | 155 | 7.2 | 7.4 | 68.2592 | yes | 7
7 | 2.3 | 50 | 115 | 6 | 7.4 | 67.4703 | yes | 7
8 | 2.4 | 50 | 120 | 5.9 | 7.4 | 68.7347 | yes | 7
9 | 2.7 | 50 | 135 | 4 | 7.4 | 81.1617 | yes | 7
10 | 2.2 | 50 | 110 | 4.5 | 7.4 | 73.9111 | yes | 7
11 | 2.8 | 50 | 140 | 5.6 | 7.4 | 73.5428 | yes | 7
12 | 3.1 | 50 | 155 | 6 | 7.5 | 76.8924 | yes | 7
13 | 2.4 | 50 | 120 | 2.4 | 7.4 | 87.5102 | yes | 7
14 | 2.2 | 50 | 110 | 3.3 | 7.4 | 80.2898 | yes | 7
15 | 3 | 50 | 150 | 4.2 | 7.4 | 82.9436 | yes | 7
16 | 2.7 | 50 | 135 | 3.3 | 7.4 | 85.1947 | yes | 7
17 | 3 | 50 | 150 | 1.7 | 7.6 | 106.3442 | yes | 7
18 | 3 | 50 | 150 | 2.1 | 7.5 | 99.6223 | yes | 7
19 | 2.5 | 50 | 125 | 4.6 | 7.4 | 76.0473 | yes | 7
20 | 2.7 | 50 | 135 | 0 | 7.5 | 111.3327 | yes | 7
21 | 3 | 50 | 150 | 2 | 7.4 | 96.6553 | yes | 7
22 | 3 | 50 | 150 | 1.4 | 7.5 | 104.6231 | yes | 7
23 | 3 | 50 | 150 | 1.7 | 7.6 | 106.3442 | yes | 7
24 | 2.8 | 50 | 140 | 1.4 | 7.7 | 110.0659 | yes | 7
25 | 2.6 | 50 | 130 | 0.2 | 7.7 | 116.9024 | yes | 7
26 | 2.8 | 50 | 140 | 5.7 | 7.5 | 75.7678 | yes | 7
27 | 2.5 | 50 | 125 | 0 | 7.5 | 108.6886 | yes | 7
28 | 2.6 | 50 | 130 | 0 | 7.5 | 110.0024 | yes | 7
29 | 2.5 | 50 | 125 | 0 | 7.5 | 108.6886 | yes | 7
30 | 2.4 | 50 | 120 | 0.5 | 7.6 | 107.6389 | yes | 7
31 | 2.4 | 50 | 120 | 2.1 | 7.6 | 96.2403 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  | 7 |  | 0 | Revised February 2012