## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-02-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.2 |  | 0.2
2 |  |  |  |  | 0.22 |  | 0.22
3 |  |  |  |  | 0.21 |  | 0.21
4 |  |  |  |  | 0.19 |  | 0.19
5 |  |  |  |  | 0.2 |  | 0.2
6 |  |  |  |  | 0.24 |  | 0.24
7 |  |  |  |  | 0.26 |  | 0.26
8 |  |  |  |  | 0.3 |  | 0.3
9 |  |  |  |  | 0.37 |  | 0.37
10 |  |  |  |  | 0.35 |  | 0.35
11 |  |  |  |  | 0.32 |  | 0.32
12 |  |  |  |  | 0.25 |  | 0.25
13 |  |  |  |  | 0.22 |  | 0.22
14 |  |  |  |  | 0.19 |  | 0.19
15 |  |  |  |  | 0.25 |  | 0.25
16 |  |  |  |  | 0.19 |  | 0.19
17 |  |  |  |  | 0.24 |  | 0.24
18 |  |  |  |  | 0.26 |  | 0.26
19 |  |  |  |  | 0.28 |  | 0.28
20 |  |  |  |  | 0.33 |  | 0.33
21 |  |  |  |  | 0.89 |  | 0.89
22 |  |  |  |  | 0.91 |  | 0.91
23 |  |  |  |  | 0.86 |  | 0.86
24 |  |  |  |  | 0.91 |  | 0.91
25 |  |  |  |  | 0.93 |  | 0.93
26 |  |  |  |  | 0.94 |  | 0.94
27 |  |  |  |  | 0.93 |  | 0.93
28 |  |  |  |  | 0.92 |  | 0.92
29 |  |  |  |  | 0 |  | 0
30 |  |  |  |  | 0 |  | 0
31 |  |  |  |  | 0 |  | 0
0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 3/03/2025
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.7 | 50 | 135 | 3 | 7.6 | 93.6821 | yes | 7
2 | 2.8 | 50 | 140 | 2.1 | 7.6 | 100.9574 | yes | 7
3 | 3 | 50 | 150 | 2.7 | 7.6 | 99.1561 | yes | 7
4 | 3 | 50 | 150 | 1.1 | 7.7 | 115.1474 | yes | 7
5 | 2.9 | 50 | 145 | 1.8 | 7.6 | 104.3424 | yes | 7
6 | 2.9 | 50 | 145 | 2.5 | 7.6 | 99.3556 | yes | 7
7 | 2.7 | 50 | 135 | 3.2 | 7.5 | 89.0226 | yes | 7
8 | 2.8 | 50 | 140 | 2.4 | 7.5 | 95.2521 | yes | 7
9 | 3 | 50 | 150 | 4 | 7.6 | 90.5626 | yes | 7
10 | 2.9 | 50 | 145 | 4.2 | 7.6 | 88.2546 | yes | 7
11 | 3 | 50 | 150 | 1 | 7.5 | 107.5976 | yes | 7
12 | 3 | 50 | 150 | 0 | 7.5 | 115.425 | yes | 7
13 | 2.9 | 50 | 145 | 0.8 | 7.7 | 116.1949 | yes | 7
14 | 2.6 | 50 | 130 | 2.2 | 7.6 | 97.8833 | yes | 7
15 | 2.9 | 50 | 145 | 2.3 | 7.6 | 100.7545 | yes | 7
16 | 3 | 50 | 150 | 2.9 | 7.6 | 97.7803 | yes | 7
17 | 2.9 | 50 | 145 | 2.5 | 7.7 | 103.1286 | yes | 7
18 | 2.8 | 50 | 140 | 3.2 | 7.6 | 93.4945 | yes | 7
19 | 2.9 | 50 | 145 | 3.6 | 7.7 | 95.4981 | yes | 7
20 | 3 | 50 | 150 | 4.9 | 7.6 | 85.0733 | yes | 7
21 | 3 | 50 | 150 | 4.1 | 7.6 | 89.9347 | yes | 7
22 | 2 | 50 | 100 | 6.9 | 7.5 | 63.5324 | yes | 7
23 | 2.1 | 50 | 105 | 6.9 | 7.5 | 64.2782 | yes | 7
24 | 2 | 50 | 100 | 6 | 7.5 | 67.5588 | yes | 7
25 | 2.2 | 50 | 110 | 9.4 | 7.5 | 54.8918 | yes | 7
26 | 2.4 | 50 | 120 | 4.7 | 7.5 | 77.4321 | yes | 7
27 | 2.5 | 50 | 125 | 6.4 | 7.5 | 69.7029 | yes | 7
28 | 2.5 | 50 | 125 | 5.6 | 7.5 | 73.6399 | yes | 7
29 | 0 | 50 | 0 | 0 | 0 | 8.3699 | yes | 7
30 | 0 | 50 | 0 | 0 | 0 | 8.3699 | yes | 7
31 | 0 | 50 | 0 | 0 | 0 | 8.3699 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  | 7 |  | 0 | Revised February 2012