## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-03-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.89 |  | 0.89
2 |  |  |  |  | 0.86 |  | 0.86
3 |  |  |  |  | 0.79 |  | 0.79
4 |  |  |  |  | 0.92 |  | 0.92
5 |  |  |  |  | 0.91 |  | 0.91
6 |  |  |  |  | 0.89 |  | 0.89
7 |  |  |  |  | 0.88 |  | 0.88
8 |  |  |  |  | 0.93 |  | 0.93
9 |  |  |  |  | 0.91 |  | 0.91
10 |  |  |  |  | 0.83 |  | 0.83
11 |  |  |  |  | 0.81 |  | 0.81
12 |  |  |  |  | 0.71 |  | 0.71
13 |  |  |  |  | 0.7 |  | 0.7
14 |  |  |  |  | 0.67 |  | 0.67
15 |  |  |  |  | 0.7 |  | 0.7
16 |  |  |  |  | 0.83 |  | 0.83
17 |  |  |  |  | 0.9 |  | 0.9
18 |  |  |  |  | 0.92 |  | 0.92
19 |  |  |  |  | 0.89 |  | 0.89
20 |  |  |  |  | 0.81 |  | 0.81
21 |  |  |  |  | 0.8 |  | 0.8
22 |  |  |  |  | 0.81 |  | 0.81
23 |  |  |  |  | 0.83 |  | 0.83
24 |  |  |  |  | 0.79 |  | 0.79
25 |  |  |  |  | 0.76 |  | 0.76
26 |  |  |  |  | 0.69 |  | 0.69
27 |  |  |  |  | 0.65 |  | 0.65
28 |  |  |  |  | 0.69 |  | 0.69
29 |  |  |  |  | 0.67 |  | 0.67
30 |  |  |  |  | 0.85 |  | 0.85
31 |  |  |  |  | 0.94 |  | 0.94
0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 4/03/2025
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.5 | 50 | 125 | 6.2 | 7.4 | 68.1313 | yes | 7
2 | 2.7 | 50 | 135 | 8.8 | 7.5 | 60.5729 | yes | 7
3 | 3 | 50 | 150 | 9.1 | 7.5 | 61.4586 | yes | 7
4 | 3 | 50 | 150 | 6.3 | 7.5 | 74.4356 | yes | 7
5 | 2.9 | 50 | 145 | 9.4 | 7.5 | 59.5237 | yes | 7
6 | 3 | 50 | 150 | 7.4 | 7.5 | 69.0191 | yes | 7
7 | 3 | 50 | 150 | 6.7 | 7.6 | 75.1199 | yes | 7
8 | 2.9 | 50 | 145 | 7.1 | 7.6 | 72.2249 | yes | 7
9 | 3 | 50 | 150 | 10.4 | 7.6 | 58.3424 | yes | 7
10 | 2.9 | 50 | 145 | 8.2 | 7.6 | 66.979 | yes | 7
11 | 3 | 50 | 150 | 5.7 | 7.7 | 83.5123 | yes | 7
12 | 3 | 50 | 150 | 7.1 | 7.6 | 73.08 | yes | 7
13 | 2.7 | 50 | 135 | 6.2 | 7.7 | 77.8578 | yes | 7
14 | 2.8 | 50 | 140 | 4.6 | 7.7 | 88.0197 | yes | 7
15 | 3 | 50 | 150 | 5.7 | 7.7 | 83.5123 | yes | 7
16 | 2.6 | 50 | 130 | 9.6 | 7.7 | 60.963 | yes | 7
17 | 2.3 | 50 | 115 | 9.4 | 7.7 | 59.6788 | yes | 7
18 | 2.3 | 50 | 115 | 7.8 | 7.7 | 66.5475 | yes | 7
19 | 3 | 50 | 150 | 7.4 | 7.7 | 74.2603 | yes | 7
20 | 3 | 50 | 150 | 6.6 | 7.7 | 78.4714 | yes | 7
21 | 2.8 | 50 | 140 | 8.3 | 7.7 | 68.1888 | yes | 7
22 | 2.6 | 50 | 130 | 8.8 | 7.7 | 64.3744 | yes | 7
23 | 2.7 | 50 | 135 | 10.4 | 7.6 | 56.351 | yes | 7
24 | 2.6 | 50 | 130 | 12.3 | 7.6 | 49.0383 | yes | 7
25 | 2.4 | 50 | 120 | 12.6 | 7.6 | 46.75 | yes | 7
26 | 2.9 | 50 | 145 | 10.5 | 7.6 | 57.2816 | yes | 7
27 | 2.7 | 50 | 135 | 11.5 | 7.6 | 52.33 | yes | 7
28 | 2.5 | 50 | 125 | 10.9 | 7.7 | 55.1865 | yes | 7
29 | 2.7 | 50 | 135 | 7.7 | 7.6 | 67.7047 | yes | 7
30 | 2.7 | 50 | 135 | 7.6 | 7.6 | 68.1697 | yes | 7
31 | 2.7 | 50 | 135 | 7.9 | 7.6 | 66.7848 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  | 7 |  | 0 | Revised February 2012