## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-04-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.92 |  | 0.92
2 |  |  |  |  | 0.92 |  | 0.92
3 |  |  |  |  | 0.71 |  | 0.71
4 |  |  |  |  | 0.62 |  | 0.62
5 |  |  |  |  | 0.58 |  | 0.58
6 |  |  |  |  | 0.56 |  | 0.56
7 |  |  |  |  | 0.52 |  | 0.52
8 |  |  |  |  | 0.48 |  | 0.48
9 |  |  |  |  | 0.55 |  | 0.55
10 |  |  |  |  | 0.5 |  | 0.5
11 |  |  |  |  | 0.55 |  | 0.55
12 |  |  |  |  | 0.58 |  | 0.58
13 |  |  |  |  | 0.58 |  | 0.58
14 |  |  |  |  | 0.58 |  | 0.58
15 |  |  |  |  | 0.61 |  | 0.61
16 |  |  |  |  | 0.35 |  | 0.35
17 |  |  |  |  | 0.43 |  | 0.43
18 |  |  |  |  | 0.29 |  | 0.29
19 |  |  |  |  | 0.42 |  | 0.42
20 |  |  |  |  | 0.36 |  | 0.36
21 |  |  |  |  | 0.3 |  | 0.3
22 |  |  |  |  | 0.3 |  | 0.3
23 |  |  |  |  | 0.32 |  | 0.32
24 |  |  |  |  | 0.31 |  | 0.31
25 |  |  |  |  | 0.35 |  | 0.35
26 |  |  |  |  | 0.31 |  | 0.31
27 |  |  |  |  | 0.33 |  | 0.33
28 |  |  |  |  | 0.34 |  | 0.34
29 |  |  |  |  | 0.35 |  | 0.35
30 |  |  |  |  | 0.49 |  | 0.49
31 |  |  |  |  | 0 |  | 0
0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 5/01/2025
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.4 | 50 | 120 | 6.4 | 7.6 | 71.4542 | yes | 7
2 | 2.5 | 50 | 125 | 7.1 | 7.6 | 68.9091 | yes | 7
3 | 2.6 | 50 | 130 | 6.7 | 7.6 | 71.6629 | yes | 7
4 | 2.7 | 50 | 135 | 5.2 | 7.6 | 80.4116 | yes | 7
5 | 2.8 | 50 | 140 | 6.3 | 7.7 | 78.2416 | yes | 7
6 | 2.6 | 50 | 130 | 8.2 | 7.7 | 67.0669 | yes | 7
7 | 2.5 | 50 | 125 | 9.7 | 7.6 | 57.7291 | yes | 7
8 | 2.8 | 50 | 140 | 9.1 | 7.6 | 62.2596 | yes | 7
9 | 2.9 | 50 | 145 | 8.4 | 7.6 | 66.0696 | yes | 7
10 | 2.7 | 50 | 135 | 9.8 | 7.6 | 58.6843 | yes | 7
11 | 2.9 | 50 | 145 | 8.3 | 7.6 | 66.5226 | yes | 7
12 | 2.5 | 50 | 125 | 7.1 | 7.6 | 68.9091 | yes | 7
13 | 2.8 | 50 | 140 | 15.6 | 7.5 | 38.6491 | yes | 7
14 | 2.7 | 50 | 135 | 12.1 | 7.5 | 48.5128 | yes | 7
15 | 2.9 | 50 | 145 | 8.9 | 7.6 | 63.8534 | yes | 7
16 | 2.6 | 50 | 130 | 14.3 | 7.5 | 41.186 | yes | 7
17 | 2.8 | 50 | 140 | 12.8 | 7.5 | 46.527 | yes | 7
18 | 3 | 50 | 150 | 15.6 | 7.5 | 39.535 | yes | 7
19 | 2.6 | 50 | 130 | 17.2 | 7.6 | 35.2488 | yes | 7
20 | 2.7 | 50 | 135 | 16.2 | 7.6 | 38.1004 | yes | 7
21 | 2.8 | 50 | 140 | 12.9 | 7.6 | 47.9493 | yes | 7
22 | 2.9 | 50 | 145 | 9.7 | 7.6 | 60.4716 | yes | 7
23 | 2.7 | 50 | 135 | 10.1 | 7.6 | 57.5049 | yes | 7
24 | 2.8 | 50 | 140 | 7.9 | 7.6 | 67.5715 | yes | 7
25 | 2.7 | 50 | 135 | 13.6 | 7.6 | 45.2658 | yes | 7
26 | 2.8 | 50 | 140 | 12.8 | 7.7 | 50.0716 | yes | 7
27 | 2.9 | 50 | 145 | 10.1 | 7.7 | 61.0197 | yes | 7
28 | 2.8 | 50 | 140 | 12.6 | 7.7 | 50.7374 | yes | 7
29 | 2.9 | 50 | 145 | 11.3 | 7.7 | 56.2573 | yes | 7
30 | 3 | 50 | 150 | 12.5 | 7.7 | 52.2384 | yes | 7
31 | 0 | 50 | 0 | 0 | 0 | 8.3699 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  | 7 |  | 0 | Revised February 2012