## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-05-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.21 |  | 0.21
2 |  |  |  |  | 0.21 |  | 0.21
3 |  |  |  |  | 0.49 |  | 0.49
4 |  |  |  |  | 0.19 |  | 0.19
5 |  |  |  |  | 0.32 |  | 0.32
6 |  |  |  |  | 0.2 |  | 0.2
7 |  |  |  |  | 0.27 |  | 0.27
8 |  |  |  |  | 0.21 |  | 0.21
9 |  |  |  |  | 0.24 |  | 0.24
10 |  |  |  |  | 0.21 |  | 0.21
11 |  |  |  |  | 0.23 |  | 0.23
12 |  |  |  |  | 0.21 |  | 0.21
13 |  |  |  |  | 0.25 |  | 0.25
14 |  |  |  |  | 0.22 |  | 0.22
15 |  |  |  |  | 0.17 |  | 0.17
16 |  |  |  |  | 0.21 |  | 0.21
17 |  |  |  |  | 0.26 |  | 0.26
18 |  |  |  |  | 0.24 |  | 0.24
19 |  |  |  |  | 0.18 |  | 0.18
20 |  |  |  |  | 0.18 |  | 0.18
21 |  |  |  |  | 0.18 |  | 0.18
22 |  |  |  |  | 0.32 |  | 0.32
23 |  |  |  |  | 0.23 |  | 0.23
24 |  |  |  |  | 0.21 |  | 0.21
25 |  |  |  |  | 0.34 |  | 0.34
26 |  |  |  |  | 0.29 |  | 0.29
27 |  |  |  |  | 0.22 |  | 0.22
28 |  |  |  |  | 0.15 |  | 0.15
29 |  |  |  |  | 0.19 |  | 0.19
30 |  |  |  |  | 0.22 |  | 0.22
31 |  |  |  |  | 0.18 |  | 0.18
0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 6/02/2025
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.9 | 50 | 145 | 13.8 | 7.7 | 47.4013 | yes | 7
2 | 2.8 | 50 | 140 | 12.2 | 7.6 | 50.509 | yes | 7
3 | 2.9 | 50 | 145 | 15.2 | 7.6 | 41.6463 | yes | 7
4 | 3 | 50 | 150 | 14.4 | 7.7 | 46.0746 | yes | 7
5 | 3 | 50 | 150 | 19.8 | 7.6 | 31.0238 | yes | 7
6 | 3 | 50 | 150 | 15.8 | 7.7 | 41.996 | yes | 7
7 | 2.8 | 50 | 140 | 16.7 | 7.7 | 38.6767 | yes | 7
8 | 2.7 | 50 | 135 | 11.9 | 7.7 | 52.7987 | yes | 7
9 | 2.6 | 50 | 130 | 9.3 | 7.7 | 62.219 | yes | 7
10 | 2.5 | 50 | 125 | 10.8 | 7.7 | 55.5598 | yes | 7
11 | 2.7 | 50 | 135 | 11.6 | 7.7 | 53.8739 | yes | 7
12 | 2.9 | 50 | 145 | 12.5 | 7.7 | 51.6528 | yes | 7
13 | 2.6 | 50 | 130 | 13.1 | 7.7 | 47.9932 | yes | 7
14 | 2.5 | 50 | 125 | 12.9 | 7.7 | 48.086 | yes | 7
15 | 2.8 | 50 | 140 | 12.1 | 7.7 | 52.6969 | yes | 7
16 | 2.8 | 50 | 140 | 11.7 | 7.7 | 54.1327 | yes | 7
17 | 2.7 | 50 | 135 | 11.4 | 7.7 | 54.6039 | yes | 7
18 | 2.4 | 50 | 120 | 12.3 | 7.7 | 49.6654 | yes | 7
19 | 2.6 | 50 | 130 | 12.8 | 7.7 | 48.9543 | yes | 7
20 | 2.7 | 50 | 135 | 13.7 | 7.7 | 46.6502 | yes | 7
21 | 2.8 | 50 | 140 | 15.8 | 7.6 | 39.5714 | yes | 7
22 | 2.7 | 50 | 135 | 12.6 | 7.7 | 50.1683 | yes | 7
23 | 2.6 | 50 | 130 | 11.9 | 7.7 | 52.1955 | yes | 7
24 | 2.4 | 50 | 120 | 9.9 | 7.6 | 56.2989 | yes | 7
25 | 3 | 50 | 150 | 11.9 | 7.7 | 54.6543 | yes | 7
26 | 2.9 | 50 | 145 | 12 | 7.7 | 53.6659 | yes | 7
27 | 2.8 | 50 | 140 | 11.9 | 7.7 | 53.4095 | yes | 7
28 | 2.9 | 50 | 145 | 13.7 | 7.7 | 47.7157 | yes | 7
29 | 2.8 | 50 | 140 | 17.8 | 7.7 | 35.9516 | yes | 7
30 | 2.9 | 50 | 145 | 21 | 7.6 | 28.3095 | yes | 7
31 | 2.9 | 50 | 145 | 14 | 7.6 | 45.091 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  |  |  | 0 | Revised February 2012