## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-06-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.22 |  | 0.22
2 |  |  |  |  | 0.27 |  | 0.27
3 |  |  |  |  | 0.25 |  | 0.25
4 |  |  |  |  | 0.26 |  | 0.26
5 |  |  |  |  | 0.31 |  | 0.31
6 |  |  |  |  | 0.23 |  | 0.23
7 |  |  |  |  | 0.2 |  | 0.2
8 |  |  |  |  | 0.27 |  | 0.27
9 |  |  |  |  | 0.32 |  | 0.32
10 |  |  |  |  | 0.28 |  | 0.28
11 |  |  |  |  | 0.2 |  | 0.2
12 |  |  |  |  | 0.39 |  | 0.39
13 |  |  |  |  | 0.23 |  | 0.23
14 |  |  |  |  | 0.28 |  | 0.28
15 |  |  |  |  | 0.29 |  | 0.29
16 |  |  |  |  | 0.29 |  | 0.29
17 |  |  |  |  | 0.33 |  | 0.33
18 |  |  |  |  | 0.33 |  | 0.33
19 |  |  |  |  | 0.43 |  | 0.43
20 |  |  |  |  | 0.31 |  | 0.31
21 |  |  |  |  | 0.24 |  | 0.24
22 |  |  |  |  | 0.36 |  | 0.36
23 |  |  |  |  | 0.36 |  | 0.36
24 |  |  |  |  | 0.35 |  | 0.35
25 |  |  |  |  | 0.24 |  | 0.24
26 |  |  |  |  | 0.3 |  | 0.3
27 |  |  |  |  | 0.4 |  | 0.4
28 |  |  |  |  | 0.45 |  | 0.45
29 |  |  |  |  | 0.34 |  | 0.34
30 |  |  |  |  | 0.31 |  | 0.31
31 | [6 empty] | 0
0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 7/02/2025
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.8 | 50 | 140 | 14.8 | 7.7 | 43.8681 | yes | 7
2 | 2.7 | 50 | 135 | 15.2 | 7.7 | 42.2407 | yes | 7
3 | 2.8 | 50 | 140 | 15.6 | 7.8 | 43.1632 | yes | 7
4 | 2.9 | 50 | 145 | 15.8 | 7.7 | 41.5234 | yes | 7
5 | 2.9 | 50 | 145 | 17.6 | 7.7 | 36.8485 | yes | 7
6 | 2.8 | 50 | 140 | 20.5 | 7.8 | 31.1674 | yes | 7
7 | 2.8 | 50 | 140 | 17 | 7.7 | 37.9141 | yes | 7
8 | 2.7 | 50 | 135 | 17.6 | 7.7 | 36.0215 | yes | 7
9 | 2.5 | 50 | 125 | 18.1 | 7.7 | 34.0606 | yes | 7
10 | 2.5 | 50 | 125 | 18.5 | 7.7 | 33.1655 | yes | 7
11 | 2.6 | 50 | 130 | 21 | 7.7 | 28.3912 | yes | 7
12 | 2.5 | 50 | 125 | 14.4 | 7.7 | 43.5431 | yes | 7
13 | 2.7 | 50 | 135 | 17.2 | 7.7 | 36.9919 | yes | 7
14 | 2.8 | 50 | 140 | 18.1 | 7.7 | 35.2416 | yes | 7
15 | 2.7 | 50 | 135 | 18.9 | 7.7 | 33.0366 | yes | 7
16 | 2.9 | 50 | 145 | 13.5 | 7.8 | 50.1581 | yes | 7
17 | 3.2 | 50 | 160 | 13.8 | 7.9 | 52.7663 | yes | 7
18 | 2.2 | 50 | 110 | 15.7 | 7.8 | 40.063 | yes | 7
19 | 2 | 50 | 100 | 14.2 | 7.8 | 43.2601 | yes | 7
20 | 2.5 | 50 | 125 | 14.5 | 7.8 | 44.8758 | yes | 7
21 | 2.7 | 50 | 135 | 13.7 | 7.9 | 50.204 | yes | 7
22 | 2.1 | 50 | 105 | 13.5 | 7.9 | 47.5413 | yes | 7
23 | 2.4 | 50 | 120 | 13 | 7.8 | 48.9991 | yes | 7
24 | 2.6 | 50 | 130 | 15.2 | 7.8 | 43.3307 | yes | 7
25 | 3.1 | 50 | 155 | 15.5 | 7.8 | 44.9489 | yes | 7
26 | 2.9 | 50 | 145 | 15.9 | 7.8 | 42.7954 | yes | 7
27 | 2.8 | 50 | 140 | 15.8 | 7.8 | 42.5952 | yes | 7
28 | 2.9 | 50 | 145 | 15.2 | 7.8 | 44.8255 | yes | 7
29 | 2.7 | 50 | 135 | 16.8 | 7.7 | 37.9878 | yes | 7
30 | 2.6 | 50 | 130 | 18 | 7.8 | 35.9847 | yes | 7
31 |  | 50 | 0 |  |  | 8.3699 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  |  |  | 0 | Revised February 2012