## Turbidity and CTs
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Yamhill
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-08-01
System Name: | Camp Yamhill |  |  | ID#: 41 | 91964 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0.31 |  | 0.31
2 |  |  |  |  | 0.32 |  | 0.32
3 |  |  |  |  | 0.36 |  | 0.36
4 |  |  |  |  | 0.41 |  | 0.41
5 |  |  |  |  | 0.29 |  | 0.29
6 |  |  |  |  | 0.29 |  | 0.29
7 |  |  |  |  | 0.29 |  | 0.29
8 |  |  |  |  | 0.28 |  | 0.28
9 |  |  |  |  | 0.28 |  | 0.28
10 |  |  |  |  | 0.27 |  | 0.27
11 |  |  |  |  | 0.29 |  | 0.29
12 |  |  |  |  | 0.28 |  | 0.28
13 |  |  |  |  | 0.25 |  | 0.25
14 |  |  |  |  | 0.25 |  | 0.25
15 |  |  |  |  | 0.28 |  | 0.28
16 |  |  |  |  | 0.36 |  | 0.36
17 |  |  |  |  | 0.3 |  | 0.3
18 |  |  |  |  | 0.27 |  | 0.27
19 |  |  |  |  | 0.25 |  | 0.25
20 |  |  |  |  | 0.25 |  | 0.25
21 |  |  |  |  | 0.29 |  | 0.29
22 |  |  |  |  | 0.26 |  | 0.26
23 |  |  |  |  | 0.3 |  | 0.3
24 |  |  |  |  | 0.2 |  | 0.2
25 |  |  |  |  | 0.15 |  | 0.15
26 |  |  |  |  | 0.21 |  | 0.21
27 |  |  |  |  | 0.29 |  | 0.29
28 |  |  |  |  | 0.21 |  | 0.21
29 |  |  |  |  | 0.19 |  | 0.19
30 |  |  |  |  | 0.4 |  | 0.4
31 |  |  |  |  | 0.35 |  | 0.35
0
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Melvin S King
[5 empty] | SIGNATURE: |  |  | DATE 9/01/2025
[5 empty] | PHONE #: (503)662-3710 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : A
System Name: | Camp Yamhill |  | ID#: 41 | 91964 | Month/Year: |  | Disinfection Giardia Log Inactiv: 1.0 | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.9 | 50 | 145 | 20.2 | 7.6 | 29.8641 | yes | 7
2 | 3 | 50 | 150 | 18.9 | 7.6 | 32.942 | yes | 7
3 | 3 | 50 | 150 | 18.6 | 7.6 | 33.6067 | yes | 7
4 | 2.9 | 50 | 145 | 17.5 | 7.7 | 37.0941 | yes | 7
5 | 2.3 | 50 | 115 | 16.8 | 7.7 | 36.3025 | yes | 7
6 | 2.5 | 50 | 125 | 19.3 | 7.7 | 31.4436 | yes | 7
7 | 2.4 | 50 | 120 | 17.2 | 7.7 | 35.7536 | yes | 7
8 | 2.1 | 50 | 105 | 16 | 7.6 | 36.0694 | yes | 7
9 | 2.2 | 50 | 110 | 16.5 | 7.6 | 35.2885 | yes | 7
10 | 2 | 50 | 100 | 27 | 7.6 | 17.0288 | yes | 7
11 | 2.1 | 50 | 105 | 26.2 | 7.6 | 18.1911 | yes | 7
12 | 2.2 | 50 | 110 | 20.8 | 7.6 | 26.4848 | yes | 7
13 | 2 | 50 | 100 | 20.6 | 7.6 | 26.2347 | yes | 7
14 | 2.8 | 50 | 140 | 21.7 | 7.6 | 26.7068 | yes | 7
15 | 2.9 | 50 | 145 | 20.9 | 7.6 | 28.4995 | yes | 7
16 | 2.6 | 50 | 130 | 20.5 | 7.6 | 28.2862 | yes | 7
17 | 2.4 | 50 | 120 | 21.8 | 7.6 | 25.3409 | yes | 7
18 | 2.4 | 50 | 120 | 21 | 7.6 | 26.7371 | yes | 7
19 | 2.4 | 50 | 120 | 18.1 | 7.6 | 32.4527 | yes | 7
20 | 2.4 | 50 | 120 | 18.9 | 7.6 | 30.7669 | yes | 7
21 | 2.7 | 50 | 135 | 16.1 | 7.6 | 38.3542 | yes | 7
22 | 2.4 | 50 | 120 | 16.3 | 7.6 | 36.582 | yes | 7
23 | 2.7 | 50 | 135 | 18.9 | 7.5 | 30.6786 | yes | 7
24 | 2.3 | 50 | 115 | 21.6 | 7.6 | 25.3907 | yes | 7
25 | 2.2 | 50 | 110 | 22 | 7.6 | 24.4362 | yes | 7
26 | 2.3 | 50 | 115 | 21.4 | 7.6 | 25.7336 | yes | 7
27 | 2.2 | 50 | 110 | 19.8 | 7.6 | 28.3183 | yes | 7
28 | 2.3 | 50 | 115 | 19 | 7.6 | 30.2159 | yes | 7
29 | 2.1 | 50 | 105 | 20.3 | 7.6 | 27.0753 | yes | 7
30 | 2 | 50 | 100 | 19.5 | 7.6 | 28.2397 | yes | 7
31 | 2.8 | 50 | 140 | 24.4 | 7.6 | 22.2766 | yes | 7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | 25 |  |  |  |  | 0 | Revised February 2012