## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-01-01
System Name: | Drift Creek Landing, LLC |  |  | ID#: 41 | 92038 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 22 | 12 | 10 | 25 | 0.13 | 2378
2 | 22 | 12 | 10 | 25 | 0.13 | 3204
3 | 22 | 12 | 10 | 25 | 0.13 | 2699
4 | 22 | 12 | 10 | 25 | 0.13 | 2285
5 | 22 | 12 | 10 | 25 | 0.13 | 2359
6 | 22 | 8 | 14 | 25 | 0.13 | 3401
7 | 22 | 8 | 14 | 25 | 0.13 | 2155
8 | 22 | 8 | 14 | 25 | 0.13 | 2314
9 | 18 | 8 | 10 | 25 | 0.13 | 2109
10 | 18 | 8 | 10 | 25 | 0.13 | 2379
11 | 20 | 8 | 12 | 25 | 0.17 | 2967
12 | 20 | 0 | 20 | 25 | 0.17 | 3305
13 | 18 | 8 | 10 | 25 | 0.17 | 2752
14 | 18 | 9 | 9 | 25 | 0.17 | 2600
15 | 18 | 9 | 9 | 25 | 0.18 | 1822
16 | 18 | 9 | 9 | 25 | 0.18 | 2987
17 | 18 | 9 | 9 | 25 | 0.18 | 2008
18 | 18 | 9 | 9 | 25 | 0.18 | 3320
19 | 18 | 9 | 9 | 25 | 0.18 | 3297
20 | 18 | 9 | 9 | 25 | 0.18 | 2310
21 | 18 | 9 | 9 | 25 | 0.18 | 1899
22 | 18 | 10 | 8 | 25 | 0.18 | 1679
23 | 18 | 10 | 8 | 25 | 0.18 | 2794
24 | 18 | 10 | 8 | 25 | 0.18 | 2087
25 | 18 | 10 | 8 | 25 | 0.16 | 3404
26 | 18 | 10 | 8 | 25 | 0.16 | 3108
27 | 18 | 10 | 8 | 25 | 0.16 | 2907
28 | 18 | 10 | 8 | 25 | 0.16 | 1978
29 | 18 | 10 | 8 | 25 | 0.16 | 1999
30 | 18 | 10 | 8 | 25 | 0.16 | 3200
31 | 18 | 10 | 8 | 25 | 0.16 | 2489
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back)
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | yes
Notes: PSI = pounds per square inch
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | Bruce Padgett |  | 2021-02-08
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 541-977-2948
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading
column may not correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form
WTP- :
System Name: | Drift Creek Landing, LLC |  | ID#: 41 | 92038 | Month/Year: | 12/17 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 3 | 26 | 78 | 14 | 7.7 | 23.6549 | YES
2 | 3.2 | 26 | 83.2 | 14 | 7.7 | 24.1951 | YES
3 | 3 | 26 | 78 | 14 | 7.7 | 23.6549 | YES
4 | 3 | 26 | 78 | 14 | 7.7 | 23.6549 | YES
5 | 3 | 26 | 78 | 13 | 7.6 | 24.3605 | YES
6 | 3 | 26 | 78 | 13 | 7.6 | 24.3605 | YES
7 | 3 | 26 | 78 | 13 | 7.7 | 25.2709 | YES
8 | 3 | 26 | 78 | 13 | 7.8 | 26.2149 | YES
9 | 3 | 26 | 78 | 13 | 7.7 | 25.2709 | YES
10 | 3 | 26 | 78 | 13 | 7.7 | 25.2709 | YES
11 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES
12 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES
13 | 3.2 | 26 | 83.2 | 13 | 7.6 | 24.9165 | YES
14 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES
15 | 3.2 | 26 | 83.2 | 12 | 7.7 | 27.7773 | YES
16 | 3.2 | 26 | 83.2 | 12 | 7.7 | 27.7773 | YES
17 | 3.2 | 26 | 83.2 | 12 | 7.7 | 27.7773 | YES
18 | 3.2 | 26 | 83.2 | 12 | 7.7 | 27.7773 | YES
19 | 3.2 | 26 | 83.2 | 12 | 7.7 | 27.7773 | YES
20 | 3.2 | 26 | 83.2 | 12 | 7.7 | 27.7773 | YES
21 | 3.2 | 26 | 83.2 | 12 | 7.7 | 27.7773 | YES
22 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES
23 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES
24 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES
25 | 3 | 26 | 78 | 13 | 7.7 | 25.2709 | YES
26 | 3 | 26 | 78 | 13 | 7.7 | 25.2709 | YES
27 | 3 | 26 | 78 | 13 | 7.7 | 25.2709 | YES
28 | 3 | 26 | 78 | 13 | 7.7 | 25.2709 | YES
29 | 3 | 26 | 78 | 13 | 7.7 | 25.2709 | YES
30 | 3 | 26 | 78 | 13 | 7.7 | 25.2709 | YES
31 | 3.2 | 26 | 83.2 | 12 | 7.7 | 27.7773 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised August 2016
Return by 10th of following month by email, fax or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2