## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-04-01
System Name: | Drift Creek Landing, LLC |  |  | ID#: 41 | 92038 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 28 | 12 | 16 | 25 | 0.13
2 | 28 | 12 | 16 | 25 | 0.13
3 | 28 | 12 | 16 | 25 | 0.13
4 | 28 | 12 | 16 | 25 | 0.13
5 | 28 | 12 | 16 | 25 | 0.13
6 | 28 | 8 | 20 | 25 | 0.13
7 | 28 | 8 | 20 | 25 | 0.13
8 | 28 | 8 | 20 | 25 | 0.13
9 | 18 | 8 | 10 | 25 | 0.13
10 | 18 | 8 | 10 | 25 | 0.13
11 | 15 | 8 | 7 | 25 | 0.17
12 | 15 | 8 | 7 | 25 | 0.17
13 | 15 | 8 | 7 | 25 | 0.17
14 | 16 | 9 | 7 | 25 | 0.17
15 | 16 | 9 | 7 | 25 | 0.18
16 | 16 | 9 | 7 | 25 | 0.18
17 | 16 | 9 | 7 | 25 | 0.18
18 | 16 | 9 | 7 | 25 | 0.18
19 | 16 | 9 | 7 | 25 | 0.18
20 | 16 | 9 | 7 | 25 | 0.18
21 | 16 | 9 | 7 | 25 | 0.18
22 | 17 | 10 | 7 | 25 | 0.18
23 | 17 | 10 | 7 | 25 | 0.18
24 | 18 | 10 | 8 | 25 | 0.18
25 | 18 | 10 | 8 | 25 | 0.16
26 | 18 | 10 | 8 | 25 | 0.16
27 | 18 | 10 | 8 | 25 | 0.16
28 | 18 | 10 | 8 | 25 | 0.16
29 | 18 | 10 | 8 | 25 | 0.16
30 | 18 | 10 | 8 | 25 | 0.16
31
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back)
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | yes
Notes: PSI = pounds per square inch
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | Bruce Padgett |  | 2021-05-07
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 541-977-2948
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading
column may not correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form
WTP- :
System Name: | Drift Creek Landing, LLC |  | ID#: 41 | 92038 | Month/Year: | 12/17 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 3.2 | 26 | 83.2 | 14 | 7.7 | 24.1951 | YES | 2368
2 | 3.2 | 26 | 83.2 | 14 | 7.7 | 24.1951 | YES | 2541
3 | 3.2 | 26 | 83.2 | 14 | 7.7 | 24.1951 | YES | 2210
4 | 3.2 | 26 | 83.2 | 14 | 7.7 | 24.1951 | YES | 2920
5 | 3.2 | 26 | 83.2 | 13 | 7.6 | 24.9165 | YES | 3110
6 | 3.2 | 26 | 83.2 | 13 | 7.6 | 24.9165 | YES | 2587
7 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES | 2354
8 | 3.2 | 26 | 83.2 | 13 | 7.8 | 26.8125 | YES | 3421
9 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES | 2100
10 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES | 2601
11 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES | 2390
12 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES | 2320
13 | 3.2 | 26 | 83.2 | 13 | 7.6 | 24.9165 | YES | 2582
14 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES | 2329
15 | 3.2 | 26 | 83.2 | 12 | 7.7 | 27.7773 | YES | 2147
16 | 3.2 | 26 | 83.2 | 12 | 7.7 | 27.7773 | YES | 3214
17 | 3.2 | 26 | 83.2 | 12 | 7.7 | 27.7773 | YES | 3009
18 | 3.2 | 26 | 83.2 | 12 | 7.7 | 27.7773 | YES | 2874
19 | 3.2 | 26 | 83.2 | 12 | 7.7 | 27.7773 | YES | 2554
20 | 3.2 | 26 | 83.2 | 12 | 7.7 | 27.7773 | YES | 2147
21 | 3.2 | 26 | 83.2 | 12 | 7.7 | 27.7773 | YES | 2028
22 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES | 2874
23 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES | 2623
24 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES | 2149
25 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES | 3201
26 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES | 3008
27 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES | 2879
28 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES | 2003
29 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES | 2109
30 | 3.2 | 26 | 83.2 | 13 | 7.7 | 25.8474 | YES | 2784
31 | [6 empty] | NO
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised August 2016
Return by 10th of following month by email, fax or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2