## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-08-01
System Name: | Drift Creek Landing, LLC |  |  | ID#: 41 | 92038 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 20 | 10 | 10 | 25 | 0.55
2 | 19 | 11 | 8 | 25 | 0.55
3 | 20 | 10 | 10 | 25 | 0.55
4 | 20 | 10 | 10 | 25 | 0.57
5 | 20 | 10 | 10 | 25 | 0.6
6 | 20 | 10 | 10 | 25 | 0.6
7 | 20 | 10 | 10 | 25 | 0.6
8 | 20 | 10 | 10 | 25 | 0.6
9 | 20 | 10 | 10 | 25 | 0.58
10 | 20 | 10 | 10 | 25 | 0.66
11 | 20 | 10 | 10 | 25 | 0.055
12 | 20 | 10 | 10 | 25 | 0.06
13 | 20 | 10 | 10 | 25 | 0.06
14 | 20 | 5 | 15 | 25 | 0.06
15 | 18 | 5 | 13 | 25 | 0.55
16 | 18 | 5 | 13 | 25 | 0.55
17 | 18 | 5 | 13 | 25 | 0.55
18 | 18 | 5 | 13 | 25 | 0.056
19 | 20 | 5 | 15 | 25 | 0.06
20 | 20 | 5 | 15 | 25 | 0.6
21 | 20 | 10 | 10 | 25 | 0.6
22 | 20 | 10 | 10 | 25 | 0.6
23 | 20 | 10 | 10 | 25 | 0.6
24 | 20 | 10 | 10 | 25 | 0.6
25 | 22 | 10 | 12 | 25 | 0.58
26 | 22 | 10 | 12 | 25 | 0.6
27 | 22 | 10 | 12 | 25 | 0.59
28 | 22 | 10 | 12 | 25 | 0.59
29 | 20 | 10 | 10 | 25 | 0.59
30 | 20 | 10 | 10 | 25 | 0.6
31
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back)
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | yes
Notes: PSI = pounds per square inch
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | Bruce Padgett |  | 2021-09-01
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 541-977-2948
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading
column may not correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form
WTP- :
System Name: | Drift Creek Landing, LLC |  | ID#: 41 | 92038 | Month/Year: | 08/21 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 3.2 | 26 | 83.2 | 15 | 6.66 | 15.4303 | YES | 2609
2 | 3.2 | 26 | 83.2 | 15 | 7.3 | 19.5468 | YES | 2322
3 | 3.2 | 26 | 83.2 | 15 | 7 | 17.4986 | YES | 2784
4 | 3.2 | 26 | 83.2 | 15 | 7.66 | 22.3162 | YES | 2655
5 | 3.2 | 26 | 83.2 | 15 | 6.37 | 13.856 | YES | 2320
6 | 3.2 | 26 | 83.2 | 15 | 5.55 | 10.2011 | YES | 2554
7 | 3.2 | 26 | 83.2 | 15.01 | 5.55 | 10.1942 | YES | 2100
8 | 3.2 | 26 | 83.2 | 15 | 5.84 | 11.372 | YES | 3210
9 | 3.2 | 26 | 83.2 | 15 | 5.85 | 11.4146 | YES | 3021
10 | 3.5 | 26 | 91 | 15 | 5.9 | 12.0376 | YES | 2097
11 | 3.5 | 26 | 91 | 14 | 6.33 | 15.1038 | YES | 2899
12 | 3.5 | 26 | 91 | 14 | 6.55 | 16.386 | YES | 2655
13 | 3.2 | 26 | 83.2 | 14 | 6.55 | 15.8359 | YES | 2741
14 | 3.2 | 26 | 83.2 | 14 | 6.55 | 15.8359 | YES | 2920
15 | 3.2 | 26 | 83.2 | 14 | 6.46 | 15.3166 | YES | 2497
16 | 3.2 | 26 | 83.2 | 14 | 6.3 | 14.4341 | YES | 2644
17 | 3.2 | 26 | 83.2 | 14 | 6.3 | 14.4341 | YES | 2983
18 | 3.2 | 26 | 83.2 | 14 | 6.33 | 14.5957 | YES | 2941
19 | 2.6 | 26 | 67.6 | 14 | 6 | 12.0525 | YES | 2874
20 | 3 | 26 | 78 | 14 | 5.87 | 12.0211 | YES | 2099
21 | 3.3 | 26 | 85.8 | 14 | 5.85 | 12.3495 | YES | 2877
22 | 3.3 | 26 | 85.8 | 14 | 5.88 | 12.4884 | YES | 3200
23 | 3.3 | 26 | 85.8 | 13 | 5.55 | 11.8089 | YES | 3091
24 | 3 | 26 | 78 | 13 | 5.87 | 12.8558 | YES | 2944
25 | 3 | 26 | 78 | 13 | 5.87 | 12.8558 | YES | 2977
26 | 3 | 26 | 78 | 13 | 5.85 | 12.7604 | YES | 2549
27 | 3.2 | 26 | 83.2 | 13 | 5.85 | 13.056 | YES | 2880
28 | 3.2 | 26 | 83.2 | 13 | 5.84 | 13.0075 | YES | 2579
29 | 3.2 | 26 | 83.2 | 14 | 5.84 | 12.1632 | YES | 2459
30 | 3.2 | 26 | 83.2 | 14 | 5.84 | 12.1632 | YES | 2994
31 | 3.2 | 26 | 83.2 | 14 | 5.89 | 12.3921 | YES | 3004
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised August 2016
Return by 10th of following month by email, fax or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2