## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-10-01
System Name: | Drift Creek Landing, LLC |  |  | ID#: 41 | 92038 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 18 | 10 | 8 | 25 | 0.56
2 | 18 | 10 | 8 | 25 | 0.56
3 | 18 | 10 | 8 | 25 | 0.56
4 | 18 | 10 | 8 | 25 | 0.56
5 | 18 | 10 | 8 | 25 | 0.57
6 | 20 | 10 | 10 | 25 | 0.57
7 | 20 | 10 | 10 | 25 | 0.58
8 | 21 | 10 | 11 | 25 | 0.57
9 | 21 | 10 | 11 | 25 | 0.56
10 | 21 | 10 | 11 | 25 | 0.56
11 | 22 | 9 | 13 | 25 | 0.56
12 | 22 | 9 | 13 | 25 | 0.55
13 | 22 | 9 | 13 | 25 | 0.55
14 | 23 | 9 | 14 | 25 | 0.56
15 | 23 | 8 | 15 | 25 | 0.56
16 | 24 | 8 | 16 | 25 | 0.56
17 | 24 | 8 | 16 | 25 | 0.56
18 | 24 | 8 | 16 | 25 | 0.56
19 | 24 | 8 | 16 | 25 | 0.56
20 | 24 | 8 | 16 | 25 | 0.55
21 | 24 | 8 | 16 | 25 | 0.55
22 | 26 | 8 | 18 | 25 | 0.55
23 | 26 | 8 | 18 | 25 | 0.55
24 | 26 | 8 | 18 | 25 | 0.55
25 | 26 | 8 | 18 | 25 | 0.56
26 | 26 | 8 | 18 | 25 | 0.56
27 | 26 | 10 | 16 | 25 | 0.56
28 | 26 | 10 | 16 | 25 | 0.55
29 | 26 | 10 | 16 | 25 | 0.56
30 | 26 | 10 | 16 | 25 | 0.56
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back)
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes
Notes: PSI = pounds per square inch
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | Bruce Padgett |  | 2021-11-08
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 541-977-2948
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading
column may not correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form
WTP- :
System Name: | Drift Creek Landing, LLC |  | ID#: 41 | 92038 | Month/Year: | 09/01/221 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 3 | 26 | 78 | 15 | 5.63 | 10.2722 | YES | 2341
2 | 3 | 26 | 78 | 15 | 5.63 | 10.2722 | YES | 3127
3 | 3.2 | 26 | 83.2 | 15 | 5.6 | 10.3944 | YES | 3210
4 | 3.1 | 26 | 80.6 | 15 | 5.6 | 10.2751 | YES | 2910
5 | 3 | 26 | 78 | 15 | 5.92 | 11.451 | YES | 2447
6 | 3.2 | 26 | 83.2 | 15 | 5.8 | 11.2032 | YES | 2600
7 | 3.2 | 26 | 83.2 | 15 | 5.6 | 10.3944 | YES | 2978
8 | 3 | 26 | 78 | 15 | 5.7 | 10.5456 | YES | 2543
9 | 3 | 26 | 78 | 15 | 5.6 | 10.1572 | YES | 2665
10 | 3 | 26 | 78 | 15 | 5.8 | 10.9482 | YES | 2978
11 | 3 | 26 | 78 | 15 | 5.8 | 10.9482 | YES | 2014
12 | 3 | 26 | 78 | 15 | 6 | 11.7985 | YES | 2366
13 | 3 | 26 | 78 | 14 | 6 | 12.6183 | YES | 2977
14 | 3 | 26 | 78 | 14 | 6.4 | 14.6419 | YES | 2543
15 | 3.2 | 26 | 83.2 | 14 | 6.4 | 14.9797 | YES | 2974
16 | 3.2 | 26 | 83.2 | 14 | 6.4 | 14.9797 | YES | 3200
17 | 3.2 | 26 | 83.2 | 14 | 6.4 | 14.9797 | YES | 3021
18 | 3.2 | 26 | 83.2 | 14 | 6.4 | 14.9797 | YES | 3208
19 | 3.2 | 26 | 83.2 | 15 | 6.2 | 13.0069 | YES | 3557
20 | 3 | 26 | 78 | 15 | 6.2 | 12.7124 | YES | 2970
21 | 3.2 | 26 | 83.2 | 15 | 6.2 | 13.0069 | YES | 2446
22 | 3.2 | 26 | 83.2 | 15 | 6.2 | 13.0069 | YES | 2335
23 | 3 | 26 | 78 | 15 | 6.2 | 12.7124 | YES | 2648
24 | 3.2 | 26 | 83.2 | 15 | 6 | 12.0725 | YES | 2797
25 | 3 | 26 | 78 | 15 | 6 | 11.7985 | YES | 2978
26 | 3 | 26 | 78 | 15 | 6 | 11.7985 | YES | 2645
27 | 3 | 26 | 78 | 15 | 5.8 | 10.9482 | YES | 2897
28 | 3.2 | 26 | 83.2 | 15 | 5.8 | 11.2032 | YES | 3031
29 | 3.2 | 26 | 83.2 | 15 | 5.8 | 11.2032 | YES | 2978
30 | 3.2 | 26 | 83.2 | 15 | 5.8 | 11.2032 | YES | 3005
31 | 3 | 26 | 78 | 15 | 5.8 | 10.9482 | YES | 2788
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised August 2016
Return by 10th of following month by email, fax or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2