## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-04-01
System Name: | Drift Creek Landing, LLC |  |  | ID#: 41 | 92038 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 34 | 20 | 14 | 25 | 0.04 | 4937
2 | 34 | 20 | 14 | 25 | 0.04 | 4934
3 | 34 | 20 | 14 | 25 | 0.04 | 5250
4 | 34 | 20 | 14 | 25 | 0.34 | 4964
5 | 34 | 20 | 14 | 25 | 0.31 | 4376
6 | 34 | 20 | 14 | 25 | 0.11 | 5172
7 | 34 | 20 | 14 | 25 | 0.1 | 6202
8 | 34 | 20 | 14 | 25 | 0.12 | 7168
9 | 34 | 20 | 14 | 25 | 0.19 | 4897
10 | 35 | 19 | 16 | 25 | 0.41 | 5393
11 | 35 | 19 | 16 | 25 | 0.91 | 5479
12 | 36 | 18 | 18 | 25 | 0.12 | 4676
13 | 36 | 18 | 18 | 25 | 0.16 | 4621
14 | 36 | 18 | 18 | 25 | 0.11 | 5087
15 | 36 | 18 | 18 | 25 | 0.08 | 4901
16 | 36 | 18 | 18 | 25 | 0.1 | 4794
17 | 36 | 18 | 18 | 25 | 0.15 | 4836
18 | 36 | 18 | 18 | 25 | 0.1 | 4884
19 | 36 | 18 | 18 | 25 | 0.12 | 5015
20 | 36 | 18 | 18 | 25 | 0.12 | 5473
21 | 36 | 18 | 18 | 25 | 0.14 | 4694
22 | 35 | 18 | 17 | 25 | 0.17 | 4795
23 | 35 | 19 | 16 | 25 | 0.17 | 5019
24 | 35 | 19 | 16 | 25 | 0.14 | 4612
25 | 35 | 19 | 16 | 25 | 0.04 | 5258
26 | 34 | 19 | 15 | 25 | 0.09 | 4209
27 | 34 | 19 | 15 | 25 | .0.6 | 4938
28 | 34 | 19 | 15 | 25 | 0.1 | 5460
29 | 34 | 19 | 15 | 25 | 0.08 | 5524
30 | 34 | 18 | 16 | 25 | 0.06 | 5185
31 |  |  |  | 25
|  |  |  | yes | CT's met everyday? (see back)
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | yes
Notes: PSI = pounds per square inch
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | Robert Skelton |  | #NAME?
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 509-770-5298
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading
column may not correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form
WTP- :
System Name: | Drift Creek Landing, LLC |  | ID#: 41 | 92038 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.1 | 26 | 28.6 | 11 | 7.05 | 18.6051 | YES
2 | 1.08 | 26 | 28.08 | 11.1 | 7.05 | 18.4444 | YES
3 | 1.07 | 26 | 27.82 | 11.1 | 7.05 | 18.424 | YES
4 | 0.74 | 26 | 19.24 | 11.3 | 7.08 | 17.7193 | YES
5 | 0.98 | 26 | 25.48 | 11.1 | 7.15 | 18.8811 | YES
6 | 0.87 | 26 | 22.62 | 10.8 | 7.16 | 19.0841 | YES
7 | 0.8 | 26 | 20.8 | 11.2 | 7.09 | 18.0136 | YES
8 | 0.78 | 26 | 20.28 | 11.2 | 7.14 | 18.2853 | YES
9 | 0.72 | 26 | 18.72 | 11.3 | 7.13 | 17.986 | YES
10 | 0.7 | 26 | 18.2 | 11.1 | 7.11 | 18.0547 | YES
11 | 0.73 | 26 | 18.98 | 10.9 | 7.18 | 18.7978 | YES
12 | 0.74 | 26 | 19.24 | 10.7 | 7.2 | 19.1966 | YES
13 | 0.78 | 26 | 20.28 | 10.2 | 7.16 | 19.6454 | YES
14 | 0.78 | 26 | 20.28 | 10 | 7.2 | 20.1821 | YES
15 | 0.79 | 26 | 20.54 | 9.9 | 7.22 | 20.4794 | YES
16 | 0.8 | 26 | 20.8 | 10 | 7.24 | 20.5112 | YES
17 | 0.79 | 26 | 20.54 | 10.1 | 7.16 | 19.7959 | YES
18 | 0.79 | 26 | 20.54 | 10.3 | 7.16 | 19.5397 | YES
19 | 0.8 | 26 | 20.8 | 10.2 | 7.2 | 19.9648 | YES
20 | 0.76 | 26 | 19.76 | 10.4 | 7.2 | 19.6184 | YES
21 | 0.75 | 26 | 19.5 | 10.8 | 7.17 | 18.8967 | YES
22 | 0.86 | 26 | 22.36 | 11 | 7.17 | 18.8824 | YES
23 | 0.84 | 26 | 21.84 | 11 | 7.2 | 19.0368 | YES
24 | 0.76 | 26 | 19.76 | 11.2 | 7.17 | 18.4342 | YES
25 | 0.75 | 26 | 19.5 | 11.6 | 7.17 | 17.9449 | YES
26 | 0.7 | 26 | 18.2 | 11.6 | 7.17 | 17.8463 | YES
27 | 0.95 | 26 | 24.7 | 11.6 | 7.2 | 18.536 | YES
28 | 0.85 | 26 | 22.1 | 11.5 | 7.18 | 18.3243 | YES
29 | 0.76 | 26 | 19.76 | 11.4 | 7.18 | 18.2604 | YES
30 | 0.82 | 26 | 21.32 | 11.6 | 7.21 | 18.3344 | YES
31 |  | 26 |  |  |  |  | NO
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised August 2016