## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-05-01
System Name: | Drift Creek Landing, LLC |  |  | ID#: 41 | 92038 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 34 | 19 | 15 | 25 | 0.31 | 5107
2 | 34 | 19 | 15 | 25 | 0.39 | 4897
3 | 34 | 19 | 15 | 25 | 0.34 | 4809
4 | 34 | 19 | 15 | 25 | 0.4 | 4488
5 | 34 | 19 | 15 | 25 | 0.39 | 4715
6 | 34 | 19 | 15 | 25 | 0.41 | 5394
7 | 34 | 19 | 15 | 25 | 0.32 | 4689
8 | 34 | 19 | 15 | 25 | 0.29 | 4922
9 | 34 | 19 | 15 | 25 | 0.16 | 5050
10 | 35 | 18 | 17 | 25 | 0.19 | 5344
11 | 35 | 18 | 17 | 25 | 0.25 | 6173
12 | 35 | 20 | 15 | 25 | 0.21 | 6789
13 | 35 | 20 | 15 | 25 | 0.27 | 5678
14 | 35 | 20 | 15 | 25 | 0.45 | 5826
15 | 35 | 20 | 15 | 25 | 0.18 | 5242
16 | 35 | 20 | 15 | 25 | 0.31 | 5295
17 | 36 | 21 | 15 | 25 | 0.21 | 5187
18 | 36 | 21 | 15 | 25 | 0.16 | 6942
19 | 38.22 | 18 | 20.22 | 25 | 0.16 | 4085
20 | 38 | 20 | 18 | 25 | 0.16 | 4000
21 | 40 | 16 | 24 | 25 | 0.22 | 5634
22 | 44 | 16 | 28 | 25 | 0.18 | 6185
23 | 38 | 19 | 19 | 25 | 0.3 | 4685
24 | 40 | 18 | 22 | 25 | 0.31 | 4882
25 | 40 | 15 | 25 | 25 | 0.21 | 5475
26 | 39 | 16 | 23 | 25 | 0.27 | 5995
27 | 38 | 16 | 22 | 25 | 0.3 | 6080
28 | 38 | 16 | 22 | 25 | 0.34 | 5587
29 | 38 | 16 | 22 | 25 | 0.18 | 5125
30 | 38 | 16 | 22 | 25 | 0.38 | 5260
31 | 42 | 14 | 28 | 25 | 0.4 | 5479
|  |  |  | yes | CT's met everyday? (see back)
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | yes
Notes: PSI = pounds per square inch
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | Robert Skelton |  | #NAME?
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 509-770-5298
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading
column may not correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form
WTP- :
System Name: | Drift Creek Landing, LLC |  | ID#: 41 | 92038 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.82 | 26 | 21.32 | 11.6 | 7.27 | 18.7173 | YES
2 | 0.77 | 26 | 20.02 | 11.7 | 7.27 | 18.4939 | YES
3 | 0.76 | 26 | 19.76 | 11.7 | 7.26 | 18.4099 | YES
4 | 0.75 | 26 | 19.5 | 11.5 | 7.28 | 18.7578 | YES
5 | 1.05 | 26 | 27.3 | 11.9 | 7.31 | 19.0934 | YES
6 | 1.02 | 26 | 26.52 | 11.9 | 7.31 | 19.0299 | YES
7 | 0.88 | 26 | 22.88 | 11.9 | 7.36 | 19.0629 | YES
8 | 0.9 | 26 | 23.4 | 11.4 | 7.3 | 19.3303 | YES
9 | 0.99 | 26 | 25.74 | 11.1 | 7.33 | 20.1193 | YES
10 | 1 | 26 | 26 | 11.3 | 7.35 | 20.0193 | YES
11 | 1.12 | 26 | 29.12 | 11.1 | 7.37 | 20.7011 | YES
12 | 1.02 | 26 | 26.52 | 11.3 | 7.29 | 19.6501 | YES
13 | 0.95 | 26 | 24.7 | 11.1 | 7.39 | 20.4525 | YES
14 | 0.75 | 26 | 19.5 | 11.8 | 7.39 | 19.1091 | YES
15 | 0.95 | 26 | 24.7 | 11.9 | 7.25 | 18.4959 | YES
16 | 0.96 | 26 | 24.96 | 12.1 | 7.33 | 18.7895 | YES
17 | 0.92 | 26 | 23.92 | 12 | 7.35 | 18.9584 | YES
18 | 0.8 | 26 | 20.8 | 11.9 | 7.35 | 18.8292 | YES
19 | 0.84 | 26 | 21.84 | 11.9 | 7.33 | 18.7828 | YES
20 | 0.9 | 26 | 23.4 | 11.9 | 7.4 | 19.3717 | YES
21 | 0.83 | 26 | 21.58 | 11.5 | 7.49 | 20.3556 | YES
22 | 0.88 | 26 | 22.88 | 12 | 7.4 | 19.2035 | YES
23 | 0.91 | 26 | 23.66 | 12.5 | 7.42 | 18.6046 | YES
24 | 0.94 | 26 | 24.44 | 12.7 | 7.41 | 18.3537 | YES |  | ]=
25 | 1.02 | 26 | 26.52 | 13.1 | 7.42 | 18.102 | YES
26 | 1.05 | 26 | 27.3 | 13.1 | 7.36 | 17.7658 | YES
27 | 0.93 | 26 | 24.18 | 13.1 | 7.42 | 17.918 | YES
28 | 0.77 | 26 | 20.02 | 13.1 | 7.44 | 17.7258 | YES
29 | 0.96 | 26 | 24.96 | 12.9 | 7.54 | 19.0444 | YES
30 | 1 | 26 | 26 | 12.6 | 7.51 | 19.3011 | YES
31 | 1.2 | 26 | 31.2 | 13.1 | 7.5 | 19.0288 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised August 2016