## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-07-22
System Name: | Drift Creek Landing, LLC |  |  | ID#: 41 | 92038 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 20 | 20 | 0 | 25 | 0.37 | 3091
2 | 20 | 22 | -2 | 25 | 0.23 | 3886
3 | 20 | 22 | -2 | 25 | 0.09 | 5267
4 | 20 | 21 | -1 | 25 | 0.05 | 3717
5 | 22 | 19 | 3 | 25 | 0.08 | 5143
6 | 32 | 18 | 14 | 25 | 0.21 | 3699
7 | 38 | 17 | 21 | 25 | 0.27 | 4526
8 | 38 | 16 | 22 | 25 | 0.35 | 4528
9 | 40 | 16 | 24 | 25 | 0.34 | 4198
10 | 37 | 17 | 20 | 25 | 0.26 | 3686
11 | 38 | 16 | 22 | 25 | 0.17 | 3674
12 | 43 | 14 | 29 | 25 | 0.09 | 4293
13 | 40 | 15 | 25 | 25 | 0.11 | 3348
14 | 40 | 15 | 25 | 25 | 0.17 | 3557
15 | 39 | 16 | 23 | 25 | 0.08 | 4559
16 | 38 | 17 | 21 | 25 | 0.11 | 4653
17 | 42 | 15 | 27 | 25 | 0.15 | 4292
18 | 42 | 15 | 27 | 25 | 0.11 | 3398
19 | 38 | 16 | 22 | 25 | 0.1 | 4901
20 | 40 | 16 | 24 | 25 | 0.14 | 5115
21 | 40 | 16 | 24 | 25 | 0.19 | 4915
22 | 41 | 15 | 26 | 25 | 0.11 | 4810
23 | 40 | 16 | 24 | 25 | 0.13 | 4659
24 | 40 | 16 | 24 | 25 | 0.08 | 3663
25 | 40 | 16 | 24 | 25 | 0.18 | 4375
26 | 22 | 21 | 1 | 25 | 0.17 | 3915
27 | 28 | 20 | 8 | 25 | 0.12 | 3994
28 | 32 | 18 | 14 | 25 | 0.16 | 4444
29 | 40 | 16 | 24 | 25 | 0.08 | 3765
30 | 42 | 14 | 28 | 25 | 0.11 | 6495
31 | 46 | 12 | 34 | 25 | 0.18 | 6580
|  |  |  | yes | CT's met everyday? (see back)
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | yes
Notes: PSI = pounds per square inch
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | Robert Skelton |  | #NAME?
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 509 770 5298
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading
column may not correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form
WTP- :
System Name: | Drift Creek Landing, LLC |  | ID#: 41 | 92038 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.99 | 26 | 25.74 | 15.3 | 7.51 | 16.1103 | YES | .
2 | 0.68 | 26 | 17.68 | 15.6 | 7.5 | 15.187 | YES
3 | 0.7 | 26 | 18.2 | 15.3 | 7.4 | 14.9643 | YES
4 | 0.64 | 26 | 16.64 | 15.3 | 7.52 | 15.5383 | YES
5 | 0.62 | 26 | 16.12 | 15.7 | 7.43 | 14.599 | YES
6 | 1.17 | 26 | 30.42 | 16.1 | 7.49 | 15.4747 | YES
7 | 1.82 | 26 | 47.32 | 16.2 | 7.62 | 17.3673 | YES
8 | 1.78 | 26 | 46.28 | 15.7 | 7.62 | 17.8731 | YES
9 | 2.14 | 26 | 55.64 | 16.8 | 7.67 | 17.6282 | YES
10 | 1.79 | 26 | 46.54 | 16.6 | 7.61 | 16.7913 | YES
11 | 2.08 | 26 | 54.08 | 16.7 | 7.68 | 17.6905 | YES
12 | 1.55 | 26 | 40.3 | 16.9 | 7.6 | 15.9566 | YES
13 | 1.66 | 26 | 43.16 | 16.8 | 7.58 | 16.1457 | YES
14 | 1.13 | 26 | 29.38 | 16.6 | 7.55 | 15.2338 | YES
15 | 0.98 | 26 | 25.48 | 16.5 | 7.53 | 14.9645 | YES
16 | 1.27 | 26 | 33.02 | 16.4 | 7.57 | 15.8033 | YES
17 | 0.95 | 26 | 24.7 | 16.5 | 7.54 | 14.9688 | YES
18 | 1.05 | 26 | 27.3 | 16.3 | 7.54 | 15.3439 | YES
19 | 0.88 | 26 | 22.88 | 16.1 | 7.5 | 15.0272 | YES
20 | 1.1 | 26 | 28.6 | 16.1 | 7.48 | 15.2949 | YES
21 | 1.05 | 26 | 27.3 | 16.2 | 7.49 | 15.163 | YES
22 | 0.98 | 26 | 25.48 | 16.3 | 7.5 | 14.9979 | YES
23 | 0.92 | 26 | 23.92 | 16.1 | 7.49 | 15.04 | YES
24 | 0.87 | 26 | 22.62 | 16.2 | 7.52 | 15.0211 | YES
25 | 1.02 | 26 | 26.52 | 16.3 | 7.469 | 14.8942 | YES
26 | 0.61 | 26 | 15.86 | 16.1 | 7.39 | 13.9883 | YES
27 | 0.67 | 26 | 17.42 | 16.3 | 7.42 | 14.053 | YES
28 | 0.62 | 26 | 16.12 | 16.6 | 7.49 | 14.0562 | YES
29 | 0.8 | 26 | 20.8 | 16.5 | 7.47 | 14.3375 | YES
30 | 0.94 | 26 | 24.44 | 16.2 | 7.52 | 15.1415 | YES
31 | 1.32 | 26 | 34.32 | 16 | 7.54 | 16.1427 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised August 2016