## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year:
System Name: | Drift Creek Landing, LLC |  |  | ID#: 41 | 92038 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 58 | 50 | 8 | 25 | 0.08 | 6559
2 | 58 | 50 | 8 | 25 | 0.11 | 6315
3 | 58 | 50 | 8 | 25 | 0.17 | 6395
4 | 58 | 50 | 8 | 25 | 0.2 | 6251
5 | 58 | 49 | 9 | 25 | 0.13 | 7025
6 | 59 | 50 | 9 | 25 | 0.09 | 7803
7 | 59 | 49 | 10 | 25 | 0.22 | 6009
8 | 59 | 49 | 10 | 25 | 0.01 | 6831
9 | 59 | 49 | 10 | 25 | 0.07 | 5051
10 | 60 | 48 | 12 | 25 | 0.21 | 5994
11 | 60 | 48 | 12 | 25 | 0.25 | 6522
12 | 60 | 48 | 12 | 25 | 0.14 | 5591
13 | 61 | 47 | 14 | 25 | 0.23 | 5955
14 | 61 | 47 | 14 | 25 | 0.18 | 5548
15 | 61 | 46 | 15 | 25 | 0.29 | 6316
16 | 60 | 46 | 14 | 25 | 0.25 | 6235
17 | 60 | 45 | 15 | 25 | 0.08 | 5575
18 | 62 | 45 | 17 | 25 | 0.11 | 5655
19 | 62 | 46 | 16 | 25 | 0.18 | 5930
20 | 62 | 46 | 16 | 25 | 0.15 | 6822
21 | 62 | 44 | 18 | 25 | 0.09 | 5852
22 | 62 | 44 | 18 | 25 | 0.21 | 5628
23 | 62 | 42 | 20 | 25 | 0.25 | 6811
24 | 62 | 42 | 20 | 25 | 0.19 | 5760
25 | 63 | 42 | 21 | 25 | 0.1 | 5515
26 | 63 | 42 | 21 | 25 | 0.16 | 5366
27 | 63 | 42 | 21 | 25 | 0.18 | 5780
28 | 63 | 41 | 22 | 25 | 0.09 | 7019
29 | 63 | 41 | 22 | 25 | 0.06 | 6038
30 | 63 | 40 | 23 | 25 | 0.07 | 8917
31 | 64 | 40 | 24 | 25 | 0.12 | 10299
|  |  |  | yes | CT's met everyday? (see back)
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | yes
Notes: PSI = pounds per square inch
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | Robert Skelton |  | #NAME?
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 509-770-5298
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading
column may not correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form
WTP- :
System Name: | Drift Creek Landing, LLC |  | ID#: 41 | 92038 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.14 | 26 | 29.64 | 10.5 | 6.05 | 13.7657 | YES
2 | 1.1 | 26 | 28.6 | 10.4 | 6.06 | 13.838 | YES
3 | 1.19 | 26 | 30.94 | 10.3 | 6.07 | 14.1039 | YES
4 | 1.25 | 26 | 32.5 | 10.4 | 6.11 | 14.2943 | YES
5 | 1.06 | 26 | 27.56 | 10.3 | 6.1 | 14.0492 | YES
6 | 0.98 | 26 | 25.48 | 10.8 | 6.04 | 13.2444 | YES
7 | 0.82 | 26 | 21.32 | 10.9 | 6.04 | 12.9448 | YES
8 | 1.15 | 26 | 29.9 | 10.9 | 6 | 13.2265 | YES
9 | 2.2 | 26 | 57.2 | 10.6 | 6.01 | 15.1152 | YES
10 | 1.26 | 26 | 32.76 | 10.3 | 6.08 | 14.2564 | YES
11 | 0.9 | 26 | 23.4 | 10.4 | 5.99 | 13.2416 | YES
12 | 2.82 | 26 | 73.32 | 10.7 | 5.52 | 13.6409 | YES
13 | 0.74 | 26 | 19.24 | 11.3 | 5.98 | 12.2885 | YES
14 | 1.02 | 26 | 26.52 | 11.1 | 5.99 | 12.8473 | YES
15 | 1.68 | 26 | 43.68 | 10.8 | 6.11 | 14.5969 | YES
16 | 2.14 | 26 | 55.64 | 10.3 | 6.11 | 15.8267 | YES
17 | 1.92 | 26 | 49.92 | 10.3 | 6.09 | 15.3516 | YES
18 | 1.39 | 26 | 36.14 | 10.6 | 6.08 | 14.188 | YES
19 | 1.09 | 26 | 28.34 | 9.9 | 6.08 | 14.3533 | YES
20 | 1.44 | 26 | 37.44 | 9.9 | 6.09 | 14.9502 | YES
21 | 1.74 | 26 | 45.24 | 9.6 | 6.07 | 15.6299 | YES
22 | 1.88 | 26 | 48.88 | 9.8 | 6.11 | 15.8817 | YES
23 | 1.79 | 26 | 46.54 | 9.2 | 6.1 | 16.2818 | YES
24 | 1.25 | 26 | 32.5 | 9.1 | 6.04 | 15.1467 | YES
25 | 1.08 | 26 | 28.08 | 9 | 6 | 14.7679 | YES
26 | 0.88 | 26 | 22.88 | 9 | 6.01 | 14.5037 | YES
27 | 1.27 | 26 | 33.02 | 9.2 | 6.02 | 14.9839 | YES
28 | 1.18 | 26 | 30.68 | 9.9 | 6.03 | 14.2534 | YES
29 | 1.19 | 26 | 30.94 | 9.1 | 6.03 | 14.9992 | YES
30 | 1.75 | 26 | 45.5 | 8.1 | 6.08 | 17.2711 | YES
31 | 2.25 | 26 | 58.5 | 7.9 | 6.1 | 18.6134 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised August 2016