## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-05-01
System Name: | Drift Creek Landing |  |  | ID#: 41 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 60 | 40 | 20 | 25 | 0.13
2 | 60 | 40 | 20 | 25 | 0.15
3 | 60 | 40 | 20 | 25 | 0.11
4 | 60 | 40 | 20 | 25 | 0.12
5 | 60 | 38 | 22 | 25 | 0.14
6 | 60 | 51 | 9 | 25 | 0.13
7 | 60 | 48 | 12 | 25 | 0.18
8 | 60 | 46 | 14 | 25 | 0.16
9 | 60 | 46 | 14 | 25 | 0.14
10 | 60 | 44 | 16 | 25 | 0.09
11 | 60 | 44 | 16 | 25 | 0.14
12 | 60 | 44 | 16 | 25 | 0.15
13 | 60 | 40 | 20 | 25 | 0.16
14 | 60 | 40 | 20 | 25 | 0.13
15 | 60 | 40 | 20 | 25 | 0.13
16 | 60 | 40 | 20 | 25 | 0.14
17 | 60 | 40 | 20 | 25 | 0.16
18 | 60 | 40 | 20 | 25 | 0.12
19 | 60 | 40 | 20 | 25 | 0.14
20 | 60 | 40 | 20 | 25 | 0.13
21 | 60 | 39 | 21 | 25 | 0.18
22 | 60 | 39 | 21 | 25 | 0.17
23 | 60 | 39 | 21 | 25 | 0.17
24 | 60 | 38 | 22 | 25 | 0.14
25 | 60 | 38 | 22 | 25 | 0.11
26 | 60 | 38 | 22 | 25 | 0.12
27 | 60 | 37 | 23 | 25 | 0.15
28 | 60 | 49 | 11 | 25 | 0.08
29 | 60 | 47 | 13 | 25 | 0.13
30 | 60 | 46 | 14 | 25 | 0.15
31 | 60 | 46 | 14 | 25 | 0.12
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Hayden Long
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:06/07/2023
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 916-712-9601 ) |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: |  |  | ID#: 41 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.71 | 20 | 34.2 | 11.4 | 5.99 | 27.1206 | YES
2 | 1.67 | 20 | 33.4 | 11.3 | 6.03 | 27.533 | YES
3 | 1.74 | 20 | 34.8 | 11.9 | 6 | 26.4697 | YES
4 | 1.71 | 20 | 34.2 | 11.9 | 5.98 | 26.2148 | YES
5 | 1.69 | 20 | 33.8 | 11.9 | 5.97 | 26.0748 | YES
6 | 1.75 | 20 | 35 | 11.8 | 6.01 | 26.748 | YES
7 | 1.7 | 20 | 34 | 12 | 6.06 | 26.7165 | YES
8 | 1.67 | 20 | 33.4 | 12.2 | 6.04 | 26.1367 | YES
9 | 1.76 | 20 | 35.2 | 12.1 | 6.04 | 26.5467 | YES
10 | 1.73 | 20 | 34.6 | 12.1 | 6.02 | 26.291 | YES
11 | 1.8 | 20 | 36 | 12.5 | 6.01 | 24.4138 | YES
12 | 1.7 | 20 | 34 | 12.8 | 5.99 | 23.4774 | YES
13 | 1.73 | 20 | 34.6 | 13.1 | 5.97 | 22.9157 | YES
14 | 1.82 | 20 | 36.4 | 13.2 | 6.01 | 23.3451 | YES
15 | 1.86 | 20 | 37.2 | 13.7 | 5 | 15.4987 | YES
16 | 1.81 | 20 | 36.2 | 13.9 | 5.96 | 21.8323 | YES
17 | 1.88 | 20 | 37.6 | 13.4 | 6.03 | 23.3664 | YES
18 | 1.79 | 20 | 35.8 | 13.9 | 6.01 | 22.1936 | YES
19 | 1.87 | 20 | 37.4 | 13.8 | 6 | 22.4661 | YES
20 | 1.82 | 20 | 36.4 | 13.7 | 5.98 | 22.3205 | YES
21 | 1.83 | 20 | 36.6 | 13.4 | 5.98 | 22.8023 | YES
22 | 1.82 | 20 | 36.4 | 13.2 | 5.97 | 22.9987 | YES
23 | 1.91 | 20 | 38.2 | 12.9 | 5.97 | 23.7115 | YES
24 | 1.86 | 20 | 37.2 | 13.2 | 6 | 23.3652 | YES
25 | 1.94 | 20 | 38.8 | 13.2 | 5.98 | 23.4053 | YES
26 | 1.88 | 20 | 37.6 | 13.3 | 5.99 | 23.1751 | YES
27 | 1.86 | 20 | 37.2 | 13.2 | 5.95 | 22.9326 | YES
28 | 1.9 | 20 | 38 | 13.2 | 5.95 | 23.0383 | YES
29 | 1.78 | 20 | 35.6 | 12.9 | 5.94 | 23.0997 | YES
30 | 1.83 | 20 | 36.6 | 13.1 | 5.96 | 23.0942 | YES
31 | 1.75 | 20 | 35 | 12.8 | 5.99 | 23.6126 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2