## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-06-01
System Name: | Drift Creek Landing |  |  | ID#: 41 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 60 | 45 | 15 | 25
2 | 60 | 45 | 15 | 25 | 0.16
3 | 60 | 43 | 17 | 25 | 0.19
4 | 60 | 42 | 18 | 25 | 0.15
5 | 60 | 41 | 19 | 25 | 0.12
6 | 60 | 41 | 19 | 25 | 0.18
7 | 60 | 41 | 19 | 25 | 0.15
8 | 60 | 41 | 19 | 25 | 0.14
9 | 60 | 40 | 20 | 25 | 0.12
10 | 60 | 40 | 20 | 25 | 0.12
11 | 60 | 40 | 20 | 25 | 0.08
12 | 60 | 40 | 20 | 25 | 0.06
13 | 60 | 40 | 20 | 25 | 0.09
14 | 60 | 41 | 19 | 25 | 0.13
15 | 60 | 40 | 20 | 25 | 0.18
16 | 60 | 40 | 20 | 25 | 0.16
17 | 60 | 49 | 11 | 25 | 0.17
18 | 60 | 46 | 14 | 25 | 0.14
19 | 60 | 45 | 15 | 25 | 0.14
20 | 60 | 43 | 17 | 25 | 0.11
21 | 60 | 43 | 17 | 25 | 0.17
22 | 60 | 41 | 19 | 25 | 0.15
23 | 60 | 41 | 19 | 25 | 0.08
24 | 60 | 41 | 19 | 25 | 0.12
25 | 60 | 41 | 19 | 25 | 0.13
26 | 60 | 40 | 20 | 25 | 0.09
27 | 60 | 40 | 20 | 25 | 0.12
28 | 60 | 40 | 20 | 25 | 0.16
29 | 60 | 39 | 21 | 25 | 0.11
30 | 60 | 39 | 21 | 25 | 0.14
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Hayden Long
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 07/05/2023
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 916 ) 712-9601 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Drift Creek Landing |  | ID#: 41 |  | Month/Year: | 2023-06-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.83 | 26 | 47.58 | 13.2 | 6.01 | 23.3719 | YES
2 | 1.79 | 26 | 46.54 | 13.2 | 5.99 | 23.0915 | YES
3 | 1.77 | 26 | 46.02 | 13.3 | 6.03 | 23.2287 | YES
4 | 1.81 | 26 | 47.06 | 13.3 | 5.96 | 22.733 | YES
5 | 1.87 | 26 | 48.62 | 13.5 | 6.03 | 23.183 | YES
6 | 1.85 | 26 | 48.1 | 13.3 | 5.95 | 22.7526 | YES
7 | 1.83 | 26 | 47.58 | 13.2 | 6.05 | 23.7237 | YES
8 | 1.86 | 26 | 48.36 | 13.4 | 6.06 | 23.5755 | YES
9 | 1.81 | 26 | 47.06 | 13.5 | 5.98 | 22.5973 | YES
10 | 1.78 | 26 | 46.28 | 13.7 | 5.97 | 22.135 | YES
11 | 1.77 | 26 | 46.02 | 13.9 | 6 | 22.0599 | YES
12 | 1.84 | 26 | 47.84 | 14.1 | 5.98 | 21.7768 | YES
13 | 1.88 | 26 | 48.88 | 14 | 5.96 | 21.861 | YES
14 | 1.83 | 26 | 47.58 | 13.7 | 6.03 | 22.7681 | YES
15 | 1.86 | 26 | 48.36 | 13.5 | 5.97 | 22.6427 | YES
16 | 1.78 | 26 | 46.28 | 13.8 | 6.01 | 22.318 | YES
17 | 1.73 | 26 | 44.98 | 13.9 | 6.03 | 22.2065 | YES
18 | 1.75 | 26 | 45.5 | 14.1 | 6.03 | 21.9597 | YES
19 | 1.82 | 26 | 47.32 | 14 | 6.05 | 22.4544 | YES
20 | 1.86 | 26 | 48.36 | 14.2 | 5.99 | 21.7617 | YES
21 | 1.89 | 26 | 49.14 | 14.3 | 5.95 | 21.3676 | YES
22 | 1.84 | 26 | 47.84 | 14.1 | 6.02 | 22.1054 | YES
23 | 1.76 | 26 | 45.76 | 14.4 | 6.05 | 21.7067 | YES
24 | 1.79 | 26 | 46.54 | 14.6 | 6.05 | 21.4899 | YES
25 | 1.85 | 26 | 48.1 | 14.5 | 6.01 | 21.4614 | YES
26 | 1.82 | 26 | 47.32 | 14.5 | 5.94 | 20.8333 | YES
27 | 1.91 | 26 | 49.66 | 14.3 | 5.96 | 21.4973 | YES
28 | 1.83 | 26 | 47.58 | 14.5 | 5.97 | 21.0933 | YES
29 | 1.88 | 26 | 48.88 | 14.2 | 5.94 | 21.4071 | YES
30 | 1.8 | 26 | 46.8 | 14 | 6 | 21.9875 | YES
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2