## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-07-01
System Name: |  |  |  | ID#: 41 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 59 | 38 | 21 | 25 | 0.13
2 | 60 | 48 | 12 | 25 | 0.16
3 | 60 | 46 | 14 | 25 | 0.08
4 | 60 | 45 | 15 | 25 | 0.12
5 | 60 | 45 | 15 | 25 | 0.09
6 | 60 | 43 | 17 | 25 | 0.06
7 | 60 | 43 | 17 | 25 | 0.13
8 | 60 | 43 | 17 | 25 | 0.13
9 | 60 | 41 | 19 | 25 | 0.14
10 | 60 | 41 | 19 | 25 | 0.19
11 | 60 | 40 | 20 | 25 | 0.12
12 | 60 | 39 | 21 | 25 | 0.15
13 | 59 | 39 | 20 | 25 | 0.15
14 | 60 | 38 | 22 | 25 | 0.17
15 | 60 | 45 | 15 | 25 | 0.11
16 | 60 | 43 | 17 | 25 | 0.09
17 | 60 | 41 | 19 | 25 | 0.12
18 | 60 | 41 | 19 | 25 | 0.08
19 | 60 | 41 | 19 | 25 | 0.07
20 | 60 | 40 | 20 | 25 | 0.05
21 | 60 | 40 | 20 | 25 | 0.05
22 | 60 | 40 | 20 | 25 | 0.06
23 | 60 | 40 | 20 | 25 | 0.04
24 | 60 | 39 | 21 | 25 | 0.08
25 | 60 | 39 | 21 | 25 | 0.09
26 | 59 | 39 | 20 | 25 | 0.03
27 | 60 | 46 | 14 | 25 | 0.08
28 | 60 | 45 | 15 | 25 | 0.1
29 | 60 | 44 | 16 | 25 | 0.07
30 | 60 | 42 | 18 | 25 | 0.13
31 | 60 | 42 | 18 | 25 | 0.1
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Hayden Long
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 08/02/2023
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (916 ) 712-9601 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: |  |  | ID#: 41 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.82 | 26 | 47.32 | 14.2 | 5.99 | 21.6617 | YES
2 | 1.87 | 26 | 48.62 | 14.2 | 5.99 | 21.7868 | YES
3 | 1.84 | 26 | 47.84 | 14.4 | 5.98 | 21.3405 | YES
4 | 1.79 | 26 | 46.54 | 14.3 | 5.96 | 21.2021 | YES
5 | 1.85 | 26 | 48.1 | 14.4 | 5.95 | 21.1262 | YES
6 | 1.88 | 26 | 48.88 | 14.5 | 5.93 | 20.8994 | YES
7 | 1.91 | 26 | 49.66 | 14.5 | 5.92 | 20.8933 | YES
8 | 1.83 | 26 | 47.58 | 14.6 | 5.94 | 20.7169 | YES
9 | 1.87 | 26 | 48.62 | 14 | 5.91 | 21.4307 | YES
10 | 1.96 | 26 | 50.96 | 14.4 | 5.89 | 20.9198 | YES
11 | 2.08 | 26 | 54.08 | 14.3 | 5.95 | 21.8404 | YES
12 | 2.01 | 26 | 52.26 | 14.3 | 5.92 | 21.4229 | YES
13 | 2.12 | 26 | 55.12 | 14.5 | 5.88 | 21.0868 | YES
14 | 1.9 | 26 | 49.4 | 14.6 | 5.86 | 20.2671 | YES
15 | 1.95 | 26 | 50.7 | 14.6 | 5.8 | 19.9302 | YES
16 | 1.88 | 26 | 48.88 | 14.9 | 5.83 | 19.5919 | YES
17 | 1.97 | 26 | 51.22 | 15.2 | 5.81 | 19.2533 | YES
18 | 1.94 | 26 | 50.44 | 15.3 | 5.77 | 18.7721 | YES
19 | 2.03 | 26 | 52.78 | 15.3 | 5.79 | 19.1121 | YES
20 | 1.85 | 26 | 48.1 | 15.2 | 5.78 | 18.7744 | YES
21 | 1.91 | 26 | 49.66 | 15.3 | 5.77 | 18.707 | YES
22 | 1.85 | 26 | 48.1 | 15.4 | 5.8 | 18.6615 | YES
23 | 1.77 | 26 | 46.02 | 15.2 | 5.75 | 18.3921 | YES
24 | 1.82 | 26 | 47.32 | 15.2 | 5.76 | 18.5688 | YES
25 | 1.89 | 26 | 49.14 | 15.1 | 5.71 | 18.4957 | YES
26 | 1.81 | 26 | 47.06 | 15 | 5.64 | 17.969 | YES
27 | 1.93 | 26 | 50.18 | 14.9 | 5.69 | 18.6941 | YES
28 | 2.06 | 26 | 53.56 | 15 | 5.67 | 18.7079 | YES
29 | 1.94 | 26 | 50.44 | 15.1 | 5.72 | 18.6734 | YES
30 | 2.12 | 26 | 55.12 | 15.2 | 5.69 | 18.7251 | YES
31 | 2.04 | 26 | 53.04 | 14.9 | 5.74 | 19.2935 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2