## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-11-01
System Name: |  |  |  | ID#: 41 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 58 | 46 | 12 | 25 | 0.2
2 | 60 | 44 | 16 | 25 | 0.17
3 | 60 | 43 | 17 | 25 | 0.22
4 | 60 | 41 | 19 | 25 | 0.18
5 | 60 | 41 | 19 | 25 | 0.11
6 | 60 | 41 | 19 | 25 | 0.19
7 | 60 | 40 | 20 | 25 | 0.13
8 | 60 | 40 | 20 | 25 | 0.16
9 | 60 | 38 | 22 | 25 | 0.25
10 | 60 | 38 | 22 | 25 | 0.18
11 | 60 | 37 | 23 | 25 | 0.14
12 | 59 | 47 | 12 | 25 | 0.2
13 | 60 | 45 | 15 | 25 | 0.29
14 | 60 | 43 | 17 | 25 | 0.23
15 | 60 | 43 | 17 | 25 | 0.2
16 | 60 | 43 | 17 | 25 | 0.24
17 | 60 | 42 | 18 | 25 | 0.17
18 | 60 | 42 | 18 | 25 | 0.22
19 | 60 | 40 | 20 | 25 | 0.15
20 | 60 | 40 | 20 | 25 | 0.1
21 | 60 | 40 | 20 | 25 | 0.09
22 | 60 | 39 | 21 | 25 | 0.18
23 | 60 | 38 | 22 | 25 | 0.3
24 | 60 | 38 | 22 | 25 | 0.21
25 | 60 | 46 | 14 | 25 | 0.17
26 | 60 | 43 | 17 | 25 | 0.16
27 | 60 | 42 | 18 | 25 | 0.23
28 | 60 | 42 | 18 | 25 | 0.19
29 | 60 | 42 | 18 | 25 | 0.12
30 | 60 | 41 | 19 | 25 | 0.16
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Hayden Long
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 12/10/2023
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (916)712-9601 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: |  |  | ID#: 41 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.94 | 26 | 50.44 | 12.2 | 5.73 | 24.3153 | YES
2 | 2.05 | 26 | 53.3 | 13.1 | 5.77 | 22.061 | YES
3 | 1.98 | 26 | 51.48 | 13.3 | 5.7 | 21.0316 | YES
4 | 2.15 | 26 | 55.9 | 12.9 | 5.74 | 22.3666 | YES
5 | 2.01 | 26 | 52.26 | 13 | 5.79 | 22.2743 | YES
6 | 1.91 | 26 | 49.66 | 12.9 | 5.82 | 22.4186 | YES
7 | 1.84 | 26 | 47.84 | 12.8 | 5.85 | 22.6418 | YES
8 | 1.96 | 26 | 50.96 | 13.1 | 5.89 | 22.8364 | YES
9 | 2.12 | 26 | 55.12 | 12.9 | 5.84 | 23.1389 | YES
10 | 1.9 | 26 | 49.4 | 12.8 | 5.84 | 22.7135 | YES
11 | 1.86 | 26 | 48.36 | 13 | 5.78 | 21.8112 | YES
12 | 1.92 | 26 | 49.92 | 13.1 | 5.82 | 22.144 | YES
13 | 1.77 | 26 | 46.02 | 12.9 | 5.77 | 21.6511 | YES
14 | 1.85 | 26 | 48.1 | 12.7 | 5.8 | 22.3982 | YES
15 | 1.94 | 26 | 50.44 | 12.8 | 5.78 | 22.3117 | YES
16 | 1.96 | 26 | 50.96 | 12.7 | 5.73 | 22.097 | YES
17 | 1.88 | 26 | 48.88 | 12.6 | 5.75 | 22.2081 | YES
18 | 1.81 | 26 | 47.06 | 12.6 | 5.79 | 22.3622 | YES
19 | 1.78 | 26 | 46.28 | 12.4 | 5.74 | 23.7081 | YES
20 | 1.72 | 26 | 44.72 | 12.1 | 5.81 | 24.5357 | YES
21 | 1.8 | 26 | 46.8 | 11.9 | 5.76 | 24.6405 | YES
22 | 1.93 | 26 | 50.18 | 12.2 | 5.7 | 24.0575 | YES
23 | 1.96 | 26 | 50.96 | 11.8 | 5.73 | 24.9619 | YES
24 | 2.05 | 26 | 53.3 | 11.7 | 5.75 | 25.5148 | YES
25 | 1.94 | 26 | 50.44 | 11.5 | 5.81 | 26.0358 | YES
26 | 1.88 | 26 | 48.88 | 11.5 | 5.87 | 26.3838 | YES
27 | 1.82 | 26 | 47.32 | 11.2 | 5.85 | 26.5309 | YES
28 | 1.85 | 26 | 48.1 | 10.6 | 5.8 | 27.1662 | YES
29 | 1.76 | 26 | 45.76 | 10.5 | 5.86 | 27.6151 | YES
30 | 1.87 | 26 | 48.62 | 10.3 | 5.82 | 27.916 | YES
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2