## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-06-01
System Name: |  |  |  | ID#: 41 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 40 | 27 | 13 | 25 | 0.14
2 | 40 | 27 | 13 | 25 | 0.08
3 | 40 | 27 | 13 | 25 | 0.17
4 | 40 | 26 | 14 | 25 | 0.13
5 | 40 | 26 | 14 | 25 | 0.17
6 | 40 | 26 | 14 | 25 | 0.16
7 | 40 | 25 | 15 | 25 | 0.12
8 | 40 | 25 | 15 | 25 | 0.18
9 | 40 | 24 | 16 | 25 | 0.08
10 | 40 | 23 | 17 | 25 | 0.1
11 | 40 | 23 | 17 | 25 | 0.13
12 | 40 | 32 | 8 | 25 | 0.11
13 | 40 | 31 | 9 | 25 | 0.15
14 | 40 | 30 | 10 | 25 | 0.12
15 | 40 | 30 | 10 | 25 | 0.14
16 | 40 | 29 | 11 | 25 | 0.08
17 | 40 | 29 | 11 | 25 | 0.1
18 | 40 | 29 | 11 | 25 | 0.03
19 | 40 | 28 | 12 | 25 | 0.07
20 | 40 | 28 | 12 | 25 | 0.12
21 | 40 | 27 | 13 | 25 | 0.08
22 | 40 | 26 | 14 | 25 | 0.12
23 | 40 | 26 | 14 | 25 | 0.17
24 | 40 | 25 | 15 | 25 | 0.11
25 | 40 | 24 | 16 | 25 | 0.09
26 | 40 | 24 | 16 | 25 | 0.16
27 | 40 | 23 | 17 | 25 | 0.14
28 | 40 | 31 | 9 | 25 | 0.1
29 | 40 | 29 | 11 | 25 | 0.15
30 | 40 | 29 | 11 | 25 | 0.19
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Hayden Long
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 07/10/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (916-712-9601) |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Drift Creek Landing |  | ID#: 41 |  | Month/Year: | 2024-06-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.93 | 26 | 50.18 | 7.4 | 5.53 | 30.574 | YES
2 | 1.97 | 26 | 51.22 | 7.5 | 5.49 | 30.1078 | YES
3 | 1.85 | 26 | 48.1 | 7.7 | 5.45 | 28.9655 | YES
4 | 1.89 | 26 | 49.14 | 7.3 | 5.48 | 30.1262 | YES
5 | 1.92 | 26 | 49.92 | 7.3 | 5.46 | 30.0221 | YES
6 | 1.88 | 26 | 48.88 | 7.1 | 5.5 | 30.679 | YES
7 | 1.83 | 26 | 47.58 | 7 | 5.52 | 30.9135 | YES
8 | 1.9 | 26 | 49.4 | 6.9 | 5.53 | 31.4508 | YES
9 | 1.97 | 26 | 51.22 | 7.2 | 5.58 | 31.6228 | YES
10 | 1.89 | 26 | 49.14 | 7.2 | 5.61 | 31.6685 | YES
11 | 1.97 | 26 | 51.22 | 6.9 | 5.64 | 32.8901 | YES
12 | 1.86 | 26 | 48.36 | 6.7 | 5.67 | 33.2511 | YES
13 | 1.92 | 26 | 49.92 | 6.9 | 5.7 | 33.384 | YES
14 | 1.87 | 26 | 48.62 | 6.5 | 5.66 | 33.6002 | YES
15 | 1.8 | 26 | 46.8 | 6.4 | 5.57 | 32.5489 | YES
16 | 1.72 | 26 | 44.72 | 6.2 | 5.45 | 31.3823 | YES
17 | 1.81 | 26 | 47.06 | 6.1 | 5.48 | 32.2151 | YES
18 | 1.78 | 26 | 46.28 | 6.2 | 5.48 | 31.9077 | YES
19 | 1.93 | 26 | 50.18 | 6.5 | 5.44 | 31.3948 | YES
20 | 1.87 | 26 | 48.62 | 6.6 | 5.41 | 30.6854 | YES
21 | 1.85 | 26 | 48.1 | 6.4 | 5.37 | 30.594 | YES
22 | 1.93 | 26 | 50.18 | 6.4 | 5.34 | 30.5501 | YES
23 | 2.05 | 26 | 53.3 | 6.3 | 5.36 | 31.3535 | YES
24 | 1.95 | 26 | 50.7 | 6.1 | 5.4 | 31.8367 | YES
25 | 1.89 | 26 | 49.14 | 6.4 | 5.35 | 30.5209 | YES
26 | 1.81 | 26 | 47.06 | 6.5 | 5.32 | 29.7704 | YES
27 | 1.82 | 26 | 47.32 | 6.6 | 5.29 | 29.3219 | YES
28 | 1.88 | 26 | 48.88 | 6.6 | 5.33 | 29.9071 | YES
29 | 1.93 | 26 | 50.18 | 6.8 | 5.31 | 29.4964 | YES
30 | 2.02 | 26 | 52.52 | 6.9 | 5.28 | 29.3021 | YES
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2