## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-09-01
System Name: |  |  |  | ID#: 41 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 40 | 28 | 12 | 25 | 0.2
2 | 40 | 27 | 13 | 25 | 0.15
3 | 40 | 27 | 13 | 25 | 0.13
4 | 40 | 26 | 14 | 25 | 0.19
5 | 40 | 25 | 15 | 25 | 0.24
6 | 40 | 32 | 8 | 25 | 0.15
7 | 40 | 31 | 9 | 25 | 0.08
8 | 40 | 30 | 10 | 25 | 0.05
9 | 40 | 30 | 10 | 25 | 0.11
10 | 40 | 29 | 11 | 25 | 0.21
11 | 40 | 29 | 11 | 25 | 0.21
12 | 40 | 29 | 11 | 25 | 0.24
13 | 40 | 29 | 11 | 25 | 0.09
14 | 40 | 27 | 13 | 25 | 0.12
15 | 40 | 27 | 13 | 25 | 0.28
16 | 40 | 26 | 14 | 25 | 0.22
17 | 40 | 26 | 14 | 25 | 0.26
18 | 40 | 25 | 15 | 25 | 0.18
19 | 40 | 31 | 9 | 25 | 0.15
20 | 40 | 31 | 9 | 25 | 0.14
21 | 40 | 29 | 11 | 25 | 0.07
22 | 40 | 29 | 11 | 25 | 0.14
23 | 40 | 28 | 12 | 25 | 0.08
24 | 40 | 28 | 12 | 25 | 0.2
25 | 40 | 28 | 12 | 25 | 0.12
26 | 40 | 28 | 12 | 25 | 0.05
27 | 40 | 26 | 14 | 25 | 0.13
28 | 40 | 26 | 14 | 25 | 0.2
29 | 40 | 31 | 9 | 25 | 0.27
30 | 40 | 29 | 11 | 25 | 0.23
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Hayden Long
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 2024-08-06
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (916) 712-9601 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: |  |  | ID#: 41 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.91 | 26 | 49.66 | 3.7 | 5.25 | 35.1028 | YES
2 | 1.95 | 26 | 50.7 | 3.6 | 5.31 | 36.2227 | YES
3 | 2 | 26 | 52 | 3.6 | 5.19 | 34.9553 | YES
4 | 2.06 | 26 | 53.56 | 4 | 5.24 | 34.8863 | YES
5 | 2.09 | 26 | 54.34 | 3.9 | 5.2 | 34.7484 | YES
6 | 2.13 | 26 | 55.38 | 4.1 | 5.23 | 34.8116 | YES
7 | 2.04 | 26 | 53.04 | 3.6 | 5.2 | 35.2296 | YES
8 | 2.01 | 26 | 52.26 | 3.2 | 5.25 | 36.6528 | YES
9 | 1.97 | 26 | 51.22 | 3.3 | 5.27 | 36.5067 | YES
10 | 1.96 | 26 | 50.96 | 2.9 | 5.22 | 36.7821 | YES
11 | 2.05 | 26 | 53.3 | 2.6 | 5.21 | 37.7484 | YES
12 | 1.96 | 26 | 50.96 | 2.6 | 5.24 | 37.7625 | YES
13 | 1.89 | 26 | 49.14 | 2.2 | 5.29 | 39.1272 | YES
14 | 1.93 | 26 | 50.18 | 2.3 | 5.32 | 39.4556 | YES
15 | 1.98 | 26 | 51.48 | 2.1 | 5.29 | 39.7804 | YES
16 | 1.99 | 26 | 51.74 | 2 | 5.26 | 39.6697 | YES
17 | 2.07 | 26 | 53.82 | 2.2 | 5.3 | 40.0601 | YES
18 | 2.12 | 26 | 55.12 | 2.1 | 5.28 | 40.2674 | YES
19 | 2.1 | 26 | 54.6 | 2.1 | 5.31 | 40.5993 | YES
20 | 2.15 | 26 | 55.9 | 1.8 | 5.25 | 40.7747 | YES
21 | 2.11 | 26 | 54.86 | 1.5 | 5.27 | 41.6876 | YES
22 | 2.05 | 26 | 53.3 | 1.2 | 5.28 | 42.3788 | YES
23 | 1.93 | 26 | 50.18 | 1.4 | 5.22 | 40.4122 | YES
24 | 1.96 | 26 | 50.96 | 1.6 | 5.19 | 39.6067 | YES
25 | 1.89 | 26 | 49.14 | 1.6 | 5.19 | 39.2985 | YES
26 | 1.93 | 26 | 50.18 | 1.5 | 5.24 | 40.4296 | YES
27 | 1.97 | 26 | 51.22 | 1.3 | 5.29 | 41.8708 | YES
28 | 2.02 | 26 | 52.52 | 1.2 | 5.33 | 42.9824 | YES
29 | 2.08 | 26 | 54.08 | 1.5 | 5.3 | 41.9854 | YES
30 | 2.11 | 26 | 54.86 | 1.8 | 5.36 | 42.1818 | YES
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2