## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-10-01
System Name: |  |  |  | ID#: 41 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 40 | 29 | 11 | 25 | 0.18
2 | 40 | 29 | 11 | 25 | 0.09
3 | 40 | 29 | 11 | 25 | 0.13
4 | 40 | 28 | 12 | 25 | 0.07
5 | 40 | 28 | 12 | 25 | 0.19
6 | 40 | 27 | 13 | 25 | 0.14
7 | 40 | 27 | 13 | 25 | 0.12
8 | 40 | 27 | 13 | 25 | 0.08
9 | 40 | 27 | 13 | 25 | 0.16
10 | 40 | 26 | 14 | 25 | 0.1
11 | 40 | 31 | 9 | 25 | 0.16
12 | 40 | 31 | 9 | 25 | 0.11
13 | 40 | 30 | 10 | 25 | 0.2
14 | 40 | 30 | 10 | 25 | 0.15
15 | 40 | 30 | 10 | 25 | 0.09
16 | 40 | 30 | 10 | 25 | 0.12
17 | 40 | 28 | 12 | 25 | 0.18
18 | 40 | 28 | 12 | 25 | 0.13
19 | 40 | 28 | 12 | 25 | 0.06
20 | 40 | 28 | 12 | 25 | 0.14
21 | 40 | 28 | 12 | 25 | 0.1
22 | 40 | 27 | 13 | 25 | 0.17
23 | 40 | 26 | 14 | 25 | 0.08
24 | 40 | 30 | 10 | 25 | 0.18
25 | 40 | 30 | 10 | 25 | 0.07
26 | 40 | 30 | 10 | 25 | 0.11
27 | 40 | 29 | 11 | 25 | 0.14
28 | 40 | 29 | 11 | 25 | 0.09
29 | 40 | 29 | 11 | 25 | 0.15
30 | 40 | 29 | 11 | 25 | 0.1
31 | 40 | 29 | 11 | 25 | 0.18
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Hayden Long
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 09/10/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (916-712-9601 ) |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: |  |  | ID#: 41 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.9 | 26 | 49.4 | 16.2 | 5.35 | 14.9895 | YES
2 | 1.85 | 26 | 48.1 | 15.5 | 5.27 | 15.1655 | YES
3 | 1.92 | 26 | 49.92 | 14.9 | 5.22 | 15.6311 | YES
4 | 1.78 | 26 | 46.28 | 14.4 | 5.25 | 16.0946 | YES
5 | 1.88 | 26 | 48.88 | 14.2 | 5.31 | 16.8864 | YES
6 | 1.94 | 26 | 50.44 | 14.8 | 5.36 | 16.6352 | YES
7 | 1.83 | 26 | 47.58 | 15.3 | 5.3 | 15.5146 | YES
8 | 1.76 | 26 | 45.76 | 15 | 5.33 | 15.8872 | YES
9 | 1.89 | 26 | 49.14 | 14.6 | 5.24 | 16.0203 | YES
10 | 1.81 | 26 | 47.06 | 14.2 | 5.29 | 16.623 | YES
11 | 1.91 | 26 | 49.66 | 14.9 | 5.32 | 16.2168 | YES
12 | 1.85 | 26 | 48.1 | 15.1 | 5.38 | 16.2509 | YES
13 | 1.93 | 26 | 50.18 | 14.8 | 5.38 | 16.7422 | YES
14 | 1.95 | 26 | 50.7 | 14.5 | 5.34 | 16.8705 | YES
15 | 2.06 | 26 | 53.56 | 14.2 | 5.37 | 17.6391 | YES
16 | 2 | 26 | 52 | 14 | 5.32 | 17.4242 | YES
17 | 1.94 | 26 | 50.44 | 14.3 | 5.29 | 16.7619 | YES
18 | 1.95 | 26 | 50.7 | 14.8 | 5.35 | 16.5917 | YES
19 | 1.88 | 26 | 48.88 | 15.6 | 5.4 | 15.8803 | YES
20 | 1.86 | 26 | 48.36 | 15.2 | 5.36 | 16.037 | YES
21 | 1.92 | 26 | 49.92 | 14.7 | 5.31 | 16.3966 | YES
22 | 1.95 | 26 | 50.7 | 14.4 | 5.33 | 16.9217 | YES
23 | 1.99 | 26 | 51.74 | 14.1 | 5.27 | 16.9622 | YES
24 | 2.06 | 26 | 53.56 | 13.8 | 5.26 | 17.3878 | YES
25 | 1.98 | 26 | 51.48 | 14.6 | 5.29 | 16.4991 | YES
26 | 1.92 | 26 | 49.92 | 15.1 | 5.33 | 16.0763 | YES
27 | 2.03 | 26 | 52.78 | 14.4 | 5.31 | 16.9511 | YES
28 | 1.93 | 26 | 50.18 | 13.8 | 5.36 | 17.7866 | YES
29 | 1.86 | 26 | 48.36 | 13.5 | 5.39 | 18.211 | YES
30 | 1.81 | 26 | 47.06 | 13.2 | 5.37 | 18.3395 | YES
31 | 1.89 | 26 | 49.14 | 13.3 | 5.34 | 18.1783 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2