## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-03-01
System Name: |  |  |  | ID#: 41 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 40 | 32 | 8 | 25 | 0.15
2 | 40 | 32 | 8 | 25 | 0.1
3 | 40 | 32 | 8 | 25 | 0.17
4 | 40 | 31 | 9 | 25 | 0.24
5 | 40 | 30 | 10 | 25 | 0.2
6 | 40 | 30 | 10 | 25 | 0.13
7 | 40 | 30 | 10 | 25 | 0.06
8 | 40 | 29 | 11 | 25 | 0.11
9 | 40 | 29 | 11 | 25 | 0.31
10 | 40 | 28 | 12 | 25 | 0.18
11 | 40 | 27 | 13 | 25 | 0.19
12 | 40 | 27 | 13 | 25 | 0.35
13 | 40 | 27 | 13 | 25 | 0.12
14 | 40 | 26 | 14 | 25 | 0.21
15 | 39 | 34 | 5 | 25 | 0.1
16 | 39 | 34 | 5 | 25 | 0.16
17 | 40 | 34 | 6 | 25 | 0.23
18 | 40 | 33 | 7 | 25 | 0.18
19 | 40 | 33 | 7 | 25 | 0
20 | 40 | 33 | 7 | 25 | 0.07
21 | 40 | 32 | 8 | 25 | 0.2
22 | 40 | 31 | 9 | 25 | 0.13
23 | 40 | 31 | 9 | 25 | 0.23
24 | 40 | 31 | 9 | 25 | 0.2
25 | 40 | 31 | 9 | 25 | 0.1
26 | 40 | 30 | 10 | 25 | 0.17
27 | 40 | 30 | 10 | 25 | 0.32
28 | 40 | 29 | 11 | 25 | 0.21
29 | 40 | 29 | 11 | 25 | 0.18
30 | 40 | 29 | 11 | 25 | 0.25
31 | 40 | 28 | 12 | 25 | 0.14
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Hayden Long
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 04/10/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (916) 712-9601 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: |  |  | ID#: 41 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.78 | 26 | 46.28 | 8.9 | 5.52 | 27.3141 | YES
2 | 1.73 | 26 | 44.98 | 8.5 | 5.47 | 27.395 | YES
3 | 1.69 | 26 | 43.94 | 8.8 | 5.55 | 27.4929 | YES
4 | 1.76 | 26 | 45.76 | 8.6 | 5.62 | 28.6994 | YES
5 | 1.7 | 26 | 44.2 | 8.7 | 5.61 | 28.2465 | YES
6 | 1.65 | 26 | 42.9 | 9.1 | 6.7 | 39.647 | YES
7 | 1.61 | 26 | 41.86 | 9.2 | 5.79 | 28.7872 | YES
8 | 1.69 | 26 | 43.94 | 8.5 | 5.73 | 29.7319 | YES
9 | 1.44 | 26 | 37.44 | 8.6 | 5.66 | 28.1088 | YES
10 | 1.58 | 26 | 41.08 | 8.6 | 5.65 | 28.4359 | YES
11 | 1.57 | 26 | 40.82 | 8.3 | 5.54 | 27.9061 | YES
12 | 1.5 | 26 | 39 | 8.6 | 5.49 | 26.7495 | YES
13 | 1.56 | 26 | 40.56 | 8.2 | 5.43 | 27.0523 | YES
14 | 1.49 | 26 | 38.74 | 8.2 | 5.54 | 27.8423 | YES
15 | 1.62 | 26 | 42.12 | 8.1 | 5.6 | 28.9754 | YES
16 | 1.58 | 26 | 41.08 | 8.5 | 5.69 | 28.9955 | YES
17 | 1.49 | 26 | 38.74 | 8.4 | 5.76 | 29.5786 | YES
18 | 1.53 | 26 | 39.78 | 7.7 | 5.88 | 32.3216 | YES
19 | 1.61 | 26 | 41.86 | 8.7 | 5.95 | 31.3348 | YES
20 | 1.65 | 26 | 42.9 | 9.2 | 5.91 | 30.0892 | YES
21 | 1.56 | 26 | 40.56 | 9 | 5.85 | 29.5776 | YES
22 | 1.66 | 26 | 43.16 | 8.2 | 5.8 | 30.9154 | YES
23 | 1.59 | 26 | 41.34 | 9.1 | 5.77 | 28.7141 | YES
24 | 1.6 | 26 | 41.6 | 9.2 | 5.75 | 28.3779 | YES
25 | 1.72 | 26 | 44.72 | 9.5 | 5.73 | 28.0262 | YES
26 | 1.6 | 26 | 41.6 | 9.6 | 5.79 | 28.0509 | YES
27 | 1.48 | 26 | 38.48 | 9.9 | 5.76 | 26.922 | YES
28 | 1.57 | 26 | 40.82 | 9.2 | 5.82 | 28.9514 | YES
29 | 1.52 | 26 | 39.52 | 9.1 | 5.74 | 28.2194 | YES
30 | 1.64 | 26 | 42.64 | 9.2 | 5.69 | 27.9392 | YES
31 | 1.59 | 26 | 41.34 | 9 | 5.77 | 28.8934 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2