## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-06-10
System Name: | Drift Creek Landing |  |  | ID#: 41 | 92038 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 40 | 30 | 10 | 25 | 0.26
2 | 40 | 29 | 11 | 25 | 0.31
3 | 40 | 30 | 10 | 25 | 0.25
4 | 40 | 28 | 12 | 25 | 0.34
5 | 40 | 27 | 13 | 25 | 0.3
6 | 40 | 26 | 14 | 25 | 0.19
7 | 40 | 34 | 6 | 25 | 0.25
8 | 40 | 33 | 7 | 25 | 0.14
9 | 40 | 32 | 8 | 25 | 0.09
10 | 40 | 32 | 8 | 25 | 0.19
11 | 40 | 32 | 8 | 25 | 0.21
12 | 40 | 32 | 8 | 25 | 0.22
13 | 40 | 31 | 9 | 25 | 0.36
14 | 40 | 31 | 9 | 25 | 0.28
15 | 40 | 29 | 11 | 25 | 0.25
16 | 40 | 29 | 11 | 25 | 0.18
17 | 40 | 29 | 11 | 25 | 0.1
18 | 40 | 29 | 11 | 25 | 0.19
19 | 40 | 27 | 13 | 25 | 0.13
20 | 40 | 32 | 8 | 25 | 0.19
21 | 40 | 31 | 9 | 25 | 0.24
22 | 40 | 31 | 9 | 25 | 0.18
23 | 40 | 30 | 10 | 25 | 0.33
24 | 40 | 30 | 10 | 25 | 0.37
25 | 40 | 30 | 10 | 25 | 0.29
26 | 40 | 30 | 10 | 25 | 0.22
27 | 40 | 29 | 11 | 25 | 0.24
28 | 40 | 29 | 11 | 25 | 0.11
29 | 40 | 29 | 11 | 25 | 0.17
30 | 40 | 28 | 12 | 25 | 0.31
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Hayden Long
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 07/10/25
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (916) 712-9601 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Drift Creek Landing |  | ID#: 41 | 92038 | Month/Year: | 2025-05-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.22 | 26 | 31.72 | 10.7 | 5.69 | 24.3945 | YES
2 | 1.25 | 26 | 32.5 | 10.7 | 5.79 | 25.2728 | YES
3 | 1.28 | 26 | 33.28 | 10.9 | 5.74 | 24.645 | YES
4 | 1.34 | 26 | 34.84 | 10.8 | 5.61 | 23.928 | YES
5 | 1.26 | 26 | 32.76 | 10.4 | 5.57 | 23.9998 | YES
6 | 1.21 | 26 | 31.46 | 10.8 | 5.52 | 22.9441 | YES
7 | 1.27 | 26 | 33.02 | 10.9 | 5.65 | 23.9183 | YES
8 | 1.25 | 26 | 32.5 | 10.9 | 5.59 | 23.4163 | YES
9 | 1.31 | 26 | 34.06 | 10.9 | 5.48 | 22.7513 | YES
10 | 1.37 | 26 | 35.62 | 10.5 | 5.61 | 24.4395 | YES
11 | 1.22 | 26 | 31.72 | 10.4 | 5.68 | 24.7608 | YES
12 | 1.29 | 26 | 33.54 | 10.5 | 5.77 | 25.5229 | YES
13 | 1.32 | 26 | 34.32 | 10.3 | 5.66 | 25.009 | YES
14 | 1.3 | 26 | 33.8 | 10.7 | 5.7 | 24.6765 | YES
15 | 1.23 | 26 | 31.98 | 10.5 | 5.69 | 24.7166 | YES
16 | 1.25 | 26 | 32.5 | 10.9 | 5.76 | 24.7274 | YES
17 | 1.08 | 26 | 28.08 | 11 | 5.83 | 24.7004 | YES
18 | 1.14 | 26 | 29.64 | 11.2 | 5.75 | 23.9331 | YES
19 | 1.06 | 26 | 27.56 | 11.3 | 5.74 | 23.5201 | YES
20 | 1.11 | 26 | 28.86 | 11.5 | 5.62 | 22.4877 | YES
21 | 1.05 | 26 | 27.3 | 11.8 | 5.66 | 22.2369 | YES
22 | 1.07 | 26 | 27.82 | 11.5 | 5.57 | 22.0469 | YES
23 | 1.01 | 26 | 26.26 | 11.7 | 5.49 | 21.1239 | YES
24 | 1.09 | 26 | 28.34 | 12.2 | 5.54 | 21.0053 | YES
25 | 1.14 | 26 | 29.64 | 12.4 | 5.44 | 20.2315 | YES
26 | 1.03 | 26 | 26.78 | 12.5 | 5.54 | 18.7322 | YES
27 | 1.1 | 26 | 28.6 | 12.5 | 5.65 | 19.6827 | YES
28 | 1.08 | 26 | 28.08 | 12.6 | 5.5 | 18.4336 | YES
29 | 1 | 26 | 26 | 12.8 | 5.62 | 18.8508 | YES
30 | 1.12 | 26 | 29.12 | 13.2 | 5.68 | 19.0282 | YES
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2