## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-08-01
System Name: | Drift Creek Landing |  |  | ID#: 41 | 92038 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 40 | 30 | 10 | 25 | 0.33
2 | 40 | 30 | 10 | 25 | 0.21
3 | 40 | 29 | 11 | 25 | 0.25
4 | 40 | 29 | 11 | 25 | 0.35
5 | 40 | 28 | 12 | 25 | 0.18
6 | 40 | 32 | 8 | 25 | 0.22
7 | 40 | 33 | 7 | 25 | 0.3
8 | 40 | 33 | 7 | 25 | 0.26
9 | 40 | 32 | 8 | 25 | 0.14
10 | 40 | 32 | 8 | 25 | 0.15
11 | 40 | 32 | 8 | 25 | 0.09
12 | 40 | 31 | 9 | 25 | 0.23
13 | 40 | 31 | 9 | 25 | 0.16
14 | 40 | 30 | 10 | 25 | 0.24
15 | 40 | 30 | 10 | 25 | 0.3
16 | 40 | 29 | 11 | 25 | 0.28
17 | 40 | 33 | 7 | 25 | 0.36
18 | 40 | 33 | 7 | 25 | 0.33
19 | 40 | 32 | 8 | 25 | 0.25
20 | 40 | 32 | 8 | 25 | 0.2
21 | 40 | 32 | 8 | 25 | 0.26
22 | 40 | 31 | 9 | 25 | 0.18
23 | 40 | 31 | 9 | 25 | 0.18
24 | 40 | 30 | 10 | 25 | 0.07
25 | 40 | 30 | 10 | 25 | 0.12
26 | 40 | 29 | 11 | 25 | 0.23
27 | 40 | 27 | 13 | 25 | 0.39
28 | 40 | 34 | 6 | 25 | 0.11
29 | 40 | 33 | 7 | 25 | 0.15
30 | 40 | 33 | 7 | 25 | 0.24
31 | 40 | 33 | 7 | 25 | 0.2
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Hayden Long
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 09/10/25
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (916) 712-9601 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Drift Creek Landing |  | ID#: 41 | 92038 | Month/Year: | 2025-05-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.23 | 26 | 31.98 | 13.9 | 5.64 | 18.1033 | YES
2 | 1.28 | 26 | 33.28 | 13.6 | 5.6 | 18.3051 | YES
3 | 1.21 | 26 | 31.46 | 13.5 | 5.53 | 17.8043 | YES
4 | 1.15 | 26 | 29.9 | 13.4 | 5.56 | 18.004 | YES
5 | 1.2 | 26 | 31.2 | 13.5 | 5.43 | 17.1241 | YES
6 | 1.36 | 26 | 35.36 | 13.5 | 5.46 | 17.6445 | YES
7 | 1.43 | 26 | 37.18 | 13.6 | 5.39 | 17.2067 | YES
8 | 1.38 | 26 | 35.88 | 13.5 | 5.55 | 18.2965 | YES
9 | 1.3 | 26 | 33.8 | 13.9 | 5.63 | 18.1821 | YES
10 | 1.34 | 26 | 34.84 | 14.2 | 5.57 | 17.4972 | YES
11 | 1.31 | 26 | 34.06 | 13.9 | 5.47 | 17.1358 | YES
12 | 1.38 | 26 | 35.88 | 13.9 | 5.49 | 17.4069 | YES
13 | 1.45 | 26 | 37.7 | 13.8 | 5.42 | 17.2076 | YES
14 | 1.48 | 26 | 38.48 | 14.1 | 5.5 | 17.4381 | YES
15 | 1.42 | 26 | 36.92 | 14.2 | 5.37 | 16.3735 | YES
16 | 1.36 | 26 | 35.36 | 14.4 | 5.48 | 16.7217 | YES
17 | 1.39 | 26 | 36.14 | 14.4 | 5.41 | 16.3411 | YES
18 | 1.39 | 26 | 36.14 | 14.5 | 5.44 | 16.4155 | YES
19 | 1.35 | 26 | 35.1 | 14.1 | 5.56 | 17.5706 | YES
20 | 1.38 | 26 | 35.88 | 14.4 | 5.65 | 17.8731 | YES
21 | 1.32 | 26 | 34.32 | 13.7 | 6.58 | 26.3649 | YES
22 | 1.39 | 26 | 36.14 | 13.6 | 5.43 | 17.3878 | YES
23 | 1.35 | 26 | 35.1 | 13.6 | 5.4 | 17.1119 | YES
24 | 1.36 | 26 | 35.36 | 13.7 | 5.52 | 17.805 | YES
25 | 1.31 | 26 | 34.06 | 13.5 | 5.59 | 18.4244 | YES
26 | 1.26 | 26 | 32.76 | 13.9 | 5.55 | 17.5595 | YES
27 | 1.29 | 26 | 33.54 | 14.6 | 5.68 | 17.6472 | YES
28 | 1.33 | 26 | 34.58 | 14.1 | 5.61 | 17.864 | YES
29 | 1.31 | 26 | 34.06 | 14 | 5.65 | 18.2169 | YES
30 | 1.36 | 26 | 35.36 | 13 | 5.53 | 18.7423 | YES
31 | 1.3 | 26 | 33.8 | 13.5 | 5.63 | 18.6826 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2