## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-09-01
System Name: | Drift Creek Landing |  |  | ID#: 41 | 92038 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 40 | 31 | 9 | 25 | 0.19
2 | 40 | 31 | 9 | 25 | 0.2
3 | 40 | 32 | 8 | 25 | 0.28
4 | 40 | 31 | 9 | 25 | 0.11
5 | 40 | 30 | 10 | 25 | 0.34
6 | 40 | 30 | 10 | 25 | 0.22
7 | 40 | 29 | 11 | 25 | 0.25
8 | 40 | 29 | 11 | 25 | 0.21
9 | 40 | 29 | 11 | 25 | 0.06
10 | 40 | 29 | 11 | 25 | 0.13
11 | 40 | 29 | 11 | 25 | 0.15
12 | 40 | 28 | 12 | 25 | 0.3
13 | 40 | 28 | 12 | 25 | 0.23
14 | 40 | 28 | 12 | 25 | 0.17
15 | 40 | 26 | 14 | 25 | 0.21
16 | 40 | 25 | 15 | 25 | 0.09
17 | 40 | 24 | 16 | 25 | 0.16
18 | 40 | 34 | 6 | 25 | 0.23
19 | 40 | 33 | 7 | 25 | 0.14
20 | 40 | 33 | 7 | 25 | 0.3
21 | 40 | 33 | 7 | 25 | 0.24
22 | 40 | 30 | 10 | 25 | 0.32
23 | 40 | 30 | 10 | 25 | 0.3
24 | 40 | 30 | 10 | 25 | 0.21
25 | 40 | 30 | 10 | 25 | 0.27
26 | 40 | 28 | 12 | 25 | 0.19
27 | 40 | 28 | 12 | 25 | 0.25
28 | 40 | 27 | 13 | 25 | 0.2
29 | 40 | 27 | 13 | 25 | 0.16
30 | 40 | 27 | 13 | 25 | 0.22
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Hayden Long
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 10/10/25
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (916) 712-9601 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Drift Creek Landing |  | ID#: 41 | 92038 | Month/Year: | 2025-05-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.33 | 26 | 34.58 | 13.8 | 5.75 | 19.2192 | YES
2 | 1.25 | 26 | 32.5 | 12.9 | 5.72 | 20.0117 | YES
3 | 1.2 | 26 | 31.2 | 12.7 | 5.6 | 19.2778 | YES
4 | 1.24 | 26 | 32.24 | 12.5 | 5.66 | 20.079 | YES
5 | 1.39 | 26 | 36.14 | 12.3 | 5.58 | 21.7904 | YES
6 | 1.37 | 26 | 35.62 | 12.7 | 5.52 | 19.0777 | YES
7 | 1.3 | 26 | 33.8 | 13.2 | 5.61 | 18.9235 | YES
8 | 1.32 | 26 | 34.32 | 13 | 5.48 | 18.3074 | YES
9 | 1.26 | 26 | 32.76 | 14.1 | 5.47 | 16.8059 | YES
10 | 1.21 | 26 | 31.46 | 14.5 | 5.4 | 15.8325 | YES
11 | 1.22 | 26 | 31.72 | 14 | 5.35 | 16.0936 | YES
12 | 1.26 | 26 | 32.76 | 14.1 | 5.4 | 16.3661 | YES
13 | 1.28 | 26 | 33.28 | 14.5 | 5.46 | 16.3297 | YES
14 | 1.25 | 26 | 32.5 | 14.2 | 5.56 | 17.2498 | YES
15 | 1.23 | 26 | 31.98 | 14.5 | 5.63 | 17.314 | YES
16 | 1.27 | 26 | 33.02 | 13.8 | 5.69 | 18.6598 | YES
17 | 1.19 | 26 | 30.94 | 14.1 | 5.62 | 17.6424 | YES
18 | 1.24 | 26 | 32.24 | 14.1 | 5.5 | 16.9582 | YES
19 | 1.19 | 26 | 30.94 | 13.9 | 5.57 | 17.5494 | YES
20 | 1.15 | 26 | 29.9 | 14 | 5.57 | 17.3496 | YES
21 | 1.09 | 26 | 28.34 | 13.9 | 5.51 | 16.9575 | YES
22 | 1.16 | 26 | 30.16 | 13.8 | 5.38 | 16.3864 | YES
23 | 1.11 | 26 | 28.86 | 13.8 | 5.44 | 16.6658 | YES
24 | 1.08 | 26 | 28.08 | 13.2 | 5.37 | 16.8486 | YES
25 | 1.03 | 26 | 26.78 | 13.4 | 5.39 | 16.6495 | YES
26 | 1.1 | 26 | 28.6 | 13.3 | 5.53 | 17.819 | YES
27 | 1.15 | 26 | 29.9 | 13.5 | 5.56 | 17.8821 | YES
28 | 1.22 | 26 | 31.72 | 13.6 | 5.49 | 17.4387 | YES
29 | 1.07 | 26 | 27.82 | 13.3 | 5.4 | 16.9055 | YES
30 | 1.12 | 26 | 29.12 | 13.4 | 5.33 | 16.4469 | YES
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2