## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-12-01
System Name: | Drift Creek Landing |  |  | ID#: 41 | 92038 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 40 | 27 | 13 | 25 | 0.22
2 | 40 | 27 | 13 | 25 | 0.28
3 | 40 | 27 | 13 | 25 | 0.31
4 | 40 | 25 | 15 | 25 | 0.14
5 | 40 | 25 | 15 | 25 | 0.34
6 | 40 | 25 | 15 | 25 | 0.3
7 | 40 | 23 | 17 | 25 | 0.27
8 | 40 | 33 | 7 | 25 | 0.09
9 | 40 | 32 | 8 | 25 | 0.15
10 | 40 | 31 | 9 | 25 | 0.18
11 | 40 | 31 | 9 | 25 | 0.12
12 | 40 | 31 | 9 | 25 | 0.28
13 | 40 | 31 | 9 | 25 | 0.21
14 | 40 | 29 | 11 | 25 | 0.14
15 | 40 | 29 | 11 | 25 | 0.11
16 | 40 | 28 | 12 | 25 | 0.32
17 | 40 | 27 | 13 | 25 | 0.29
18 | 40 | 27 | 13 | 25 | 0.27
19 | 40 | 25 | 15 | 25 | 0.43
20 | 40 | 22 | 18 | 25 | 0.39
21 | 40 | 31 | 9 | 25 | 0.23
22 | 40 | 30 | 10 | 25 | 0.25
23 | 40 | 30 | 10 | 25 | 0.31
24 | 40 | 30 | 10 | 25 | 0.27
25 | 40 | 28 | 12 | 25 | 0.13
26 | 40 | 28 | 12 | 25 | 0.22
27 | 40 | 27 | 13 | 25 | 0.2
28 | 40 | 26 | 14 | 25 | 0.08
29 | 40 | 26 | 14 | 25 | 0.14
30 | 40 | 26 | 14 | 25 | 0.35
31 | 40 | 25 | 15 | 25 | 0.29
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Hayden Long
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 01/10/25
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (916) 712-9601 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Drift Creek Landing |  | ID#: 41 | 92038 | Month/Year: | 2025-12-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.31 | 26 | 34.06 | 10.2 | 5.36 | 22.8333 | YES
2 | 1.26 | 26 | 32.76 | 10.1 | 5.42 | 23.2924 | YES
3 | 1.2 | 26 | 31.2 | 10.3 | 5.3 | 22.0259 | YES
4 | 1.29 | 26 | 33.54 | 10.2 | 5.27 | 22.1487 | YES
5 | 1.22 | 26 | 31.72 | 10.1 | 5.39 | 22.9774 | YES
6 | 1.18 | 26 | 30.68 | 10.2 | 5.45 | 23.1854 | YES
7 | 1.27 | 26 | 33.02 | 10.8 | 5.49 | 22.8662 | YES
8 | 1.19 | 26 | 30.94 | 11 | 5.63 | 23.4309 | YES
9 | 1.25 | 26 | 32.5 | 11.2 | 5.66 | 23.5188 | YES
10 | 1.13 | 26 | 29.38 | 11.5 | 5.7 | 23.1117 | YES
11 | 1.18 | 26 | 30.68 | 11.9 | 5.69 | 22.6119 | YES
12 | 1.09 | 26 | 28.34 | 10.7 | 5.88 | 25.5909 | YES
13 | 1.01 | 26 | 26.26 | 11.2 | 5.69 | 23.1686 | YES
14 | 1.21 | 26 | 31.46 | 11 | 5.37 | 21.6281 | YES
15 | 1.12 | 26 | 29.12 | 11.1 | 5.42 | 21.6437 | YES
16 | 1.17 | 26 | 30.42 | 11.7 | 5.87 | 24.2093 | YES
17 | 1.07 | 26 | 27.82 | 11.5 | 5.82 | 23.8658 | YES
18 | 1.1 | 26 | 28.6 | 11.3 | 5.43 | 21.4153 | YES
19 | 1.22 | 26 | 31.72 | 11.1 | 5.5 | 22.4198 | YES
20 | 1.15 | 26 | 29.9 | 10.9 | 5.56 | 22.9583 | YES
21 | 1.08 | 26 | 28.08 | 10.8 | 5.65 | 23.5972 | YES
22 | 1.23 | 26 | 31.98 | 10.2 | 5.43 | 23.1565 | YES
23 | 1.14 | 26 | 29.64 | 10.4 | 5.45 | 22.8177 | YES
24 | 1.2 | 26 | 31.2 | 10.3 | 5.57 | 23.9958 | YES
25 | 1.21 | 26 | 31.46 | 10.2 | 5.49 | 23.5549 | YES
26 | 1.17 | 26 | 30.42 | 10.1 | 5.5 | 23.6748 | YES
27 | 1.12 | 26 | 29.12 | 9.8 | 5.66 | 25.2493 | YES
28 | 1.17 | 26 | 30.42 | 9.8 | 5.58 | 24.7332 | YES
29 | 1.15 | 26 | 29.9 | 9.5 | 5.56 | 24.9727 | YES
30 | 1.09 | 26 | 28.34 | 9.4 | 5.49 | 24.4117 | YES
31 | 1.03 | 26 | 26.78 | 9 | 5.32 | 23.535 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2