## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2026-02-01
System Name: | Drift Creek Landing |  |  | ID#: 41 | 92038 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 40 | 27 | 13 | 25 | 0.26
2 | 40 | 26 | 14 | 25 | 0.21
3 | 40 | 35 | 5 | 25 | 0.29
4 | 40 | 34 | 6 | 25 | 0.12
5 | 40 | 34 | 6 | 25 | 0.17
6 | 40 | 34 | 6 | 25 | 0.28
7 | 40 | 32 | 8 | 25 | 0.24
8 | 40 | 32 | 8 | 25 | 0.26
9 | 40 | 32 | 8 | 25 | 0.11
10 | 40 | 32 | 8 | 25 | 0.2
11 | 40 | 31 | 9 | 25 | 0.15
12 | 40 | 31 | 9 | 25 | 0.29
13 | 40 | 30 | 10 | 25 | 0.18
14 | 40 | 30 | 10 | 25 | 0.25
15 | 40 | 27 | 13 | 25 | 0.31
16 | 40 | 34 | 6 | 25 | 0.28
17 | 40 | 34 | 6 | 25 | 0.17
18 | 40 | 33 | 7 | 25 | 0.36
19 | 40 | 33 | 7 | 25 | 0.3
20 | 40 | 32 | 8 | 25 | 0.21
21 | 40 | 32 | 8 | 25 | 0.25
22 | 40 | 32 | 8 | 25 | 0.08
23 | 40 | 32 | 8 | 25 | 0.15
24 | 40 | 32 | 8 | 25 | 0.12
25 | 40 | 31 | 9 | 25 | 0.19
26 | 40 | 31 | 9 | 25 | 0.33
27 | 40 | 31 | 9 | 25 | 0.2
28 | 40 | 29 | 11 | 25 | 0.09
29
30
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Hayden Long
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 03/10/25
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (916) 712-9601 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Drift Creek Landing |  | ID#: 41 | 92038 | Month/Year: | 2026-01-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.08 | 26 | 28.08 | 9.2 | 5.49 | 24.6828 | YES
2 | 1.1 | 26 | 28.6 | 10.3 | 5.25 | 21.4666 | YES
3 | 1.15 | 26 | 29.9 | 9.5 | 5.17 | 22.054 | YES
4 | 1.12 | 26 | 29.12 | 9.7 | 5.43 | 23.5918 | YES
5 | 1.21 | 26 | 31.46 | 9.6 | 5.4 | 23.7254 | YES
6 | 1.28 | 26 | 33.28 | 9.9 | 5.56 | 24.7059 | YES
7 | 1.22 | 26 | 31.72 | 10.5 | 5.5 | 23.2338 | YES
8 | 1.21 | 26 | 31.46 | 10.2 | 5.53 | 23.8578 | YES
9 | 1.13 | 26 | 29.38 | 9.5 | 5.48 | 24.2872 | YES
10 | 1.17 | 26 | 30.42 | 9.3 | 5.45 | 24.4468 | YES
11 | 1.03 | 26 | 26.78 | 9.4 | 5.34 | 23.126 | YES
12 | 1.29 | 26 | 33.54 | 9.5 | 5.27 | 23.0877 | YES
13 | 1.34 | 26 | 34.84 | 9.6 | 5.25 | 22.922 | YES
14 | 1.26 | 26 | 32.76 | 9.7 | 5.27 | 22.745 | YES
15 | 1.28 | 26 | 33.28 | 9.6 | 5.43 | 24.1274 | YES
16 | 1.22 | 26 | 31.72 | 8.7 | 5.37 | 24.833 | YES
17 | 1.2 | 26 | 31.2 | 8.2 | 5.58 | 27.3589 | YES
18 | 1.3 | 26 | 33.8 | 8.2 | 5.53 | 27.1988 | YES
19 | 1.26 | 26 | 32.76 | 8.9 | 5.56 | 26.201 | YES
20 | 1.21 | 26 | 31.46 | 8.1 | 5.5 | 26.8429 | YES
21 | 1.17 | 26 | 30.42 | 8.5 | 5.57 | 26.6859 | YES
22 | 1.22 | 26 | 31.72 | 8.7 | 5.56 | 26.4128 | YES
23 | 1.29 | 26 | 33.54 | 8.5 | 5.22 | 24.1247 | YES
24 | 1.31 | 26 | 34.06 | 8.9 | 5.36 | 24.6844 | YES
25 | 1.25 | 26 | 32.5 | 8.8 | 5.32 | 24.3647 | YES
26 | 1.2 | 26 | 31.2 | 8.6 | 5.28 | 24.2201 | YES
27 | 1.26 | 26 | 32.76 | 8.8 | 5.34 | 24.5473 | YES
28 | 1.18 | 26 | 30.68 | 9 | 5.39 | 24.443 | YES
29 |  | 26
30 |  | 26
31 |  | 26
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2