## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lincoln
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 101/2025
System Name: | Alsea River RV Park & Marina |  |  | ID#: 41 | 92043 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  |  | 0
2 |  |  |  |  | 0
3 |  |  |  |  | 0
4 |  |  |  |  | 0
5 |  |  |  |  | 0
6 |  |  |  |  | 0
7 |  |  |  |  | 0
8 |  |  |  |  | 0
9 |  |  |  |  | 0
10 |  |  |  |  | 0
11 |  |  |  |  | 0
12 |  |  |  |  | 0
13 |  |  |  |  | 0
14 |  |  |  |  | 0
15 |  |  |  |  | 0
16 |  |  |  |  | 0
17 |  |  |  |  | 0
18 |  |  |  |  | 0
19 |  |  |  |  | 0
20 |  |  |  |  | 0
21 |  |  |  |  | 0
22 |  |  |  |  | 0
23 |  |  |  |  | 0
24 |  |  |  |  | 0
25 |  |  |  |  | 0
26 |  |  |  |  | 0
27 |  |  |  |  | 0
28 |  |  |  |  | 0
29 |  |  |  |  | 0
30 |  |  |  |  | 0
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Nancy Johnston
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Nancy Johnston |  | DATE:11/10/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 )563-3401 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | a
System Name: | Alsea River RV Park & Marina |  | ID#: 41 | 92043 | Month/Year: | 2025-10-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.91 | 104 | 94.64 | 14.3 | 7 | 28.2516 | YES
2 | 0.9 | 104 | 93.6 | 14.3 | 7 | 28.2194 | YES
3 | 0.9 | 104 | 93.6 | 14.5 | 7 | 27.8444 | YES
4 | 0.88 | 104 | 91.52 | 14.4 | 6.9 | 26.9467 | YES
5 | 0.88 | 104 | 91.52 | 14.5 | 7 | 27.7808 | YES
6 | 0.89 | 104 | 92.56 | 14.5 | 7 | 27.8126 | YES
7 | 0.89 | 104 | 92.56 | 14.5 | 6.9 | 26.7975 | YES
8 | 0.88 | 104 | 91.52 | 14.6 | 6.9 | 26.5882 | YES
9 | 0.87 | 104 | 90.48 | 14.6 | 6.9 | 26.5578 | YES
10 | 0.86 | 104 | 89.44 | 14.8 | 6.9 | 26.1742 | YES
11 | 0.86 | 104 | 89.44 | 14.7 | 6.9 | 26.3502 | YES
12 | 0.88 | 104 | 91.52 | 14.6 | 6.8 | 25.6165 | YES
13 | 0.9 | 104 | 93.6 | 14.6 | 6.8 | 25.6752 | YES
14 | 0.91 | 104 | 94.64 | 14.6 | 6.7 | 24.7643 | YES
15 | 0.92 | 104 | 95.68 | 14.6 | 6.7 | 24.7927 | YES
16 | 0.94 | 104 | 97.76 | 14.6 | 6.7 | 24.8497 | YES
17 | 0.94 | 104 | 97.76 | 14.6 | 6.8 | 25.7931 | YES
18 | 0.94 | 104 | 97.76 | 14.7 | 6.8 | 25.6207 | YES
19 | 0.93 | 104 | 96.72 | 14.7 | 6.76 | 25.2128 | YES
20 | 0.93 | 104 | 96.72 | 14.6 | 6.7 | 24.8212 | YES
21 | 0.92 | 104 | 95.68 | 14.6 | 6.8 | 25.7341 | YES
22 | 0.94 | 104 | 97.76 | 14.6 | 6.8 | 25.7931 | YES
23 | 0.93 | 104 | 96.72 | 14.7 | 6.8 | 25.5914 | YES
24 | 0.93 | 104 | 96.72 | 14.7 | 6.8 | 25.5914 | YES
25 | 0.93 | 104 | 96.72 | 14.5 | 6.7 | 24.9884 | YES
26 | 0.93 | 104 | 96.72 | 14.7 | 6.8 | 25.5914 | YES
27 | 0.92 | 104 | 95.68 | 14.7 | 6.8 | 25.5621 | YES
28 | 0.92 | 104 | 95.68 | 14.6 | 6.8 | 25.7341 | YES
29 | 0.92 | 104 | 95.68 | 14.6 | 6.8 | 25.7341 | YES
30 | 0.92 | 104 | 95.68 | 14.6 | 6.9 | 26.7101 | YES
31 | 0.91 | 104 | 94.64 | 14.7 | 6.8 | 25.5328 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2