## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Clackamas
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-02-01
System Name: | USFS Timberline Lodge 1 |  |  | ID#: 41-92641 |  | WTP ID: WTP- B TP for surface water
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 162 | 161 | 1 | 5 | 0.26
2 | 161 | 161 | 0 | 5 | 0.26
3 | 161 | 161 | 0 | 5 | 0.64
4 | 161 | 161 | 0 | 5 | 0.16
5 | 162 | 160 | 2 | 5 | 0.08
6 | 163 | 163 | 0 | 5 | 0.05
7 | 160 | 160 | 0 | 5 | 0.11
8 | 160 | 160 | 0 | 5 | 0.31
9 | 161 | 161 | 0 | 5 | 0.21
10 | 162 | 162 | 0 | 5 | 0.5
11 | 160 | 160 | 0 | 5 | 0.23
12 | 161 | 161 | 0 | 5 | 0.21
13 | 160 | 160 | 0 | 5 | 0.5
14 | 161 | 161 | 0 | 5 | 0.34
15 | 162 | 162 | 0 | 5 | 0.04
16 | 161 | 161 | 0 | 5 | 0.5
17 | 150 | 150 | 0 | 5 | 0.38
18 | 161 | 161 | 0 | 5 | 0.11
19 | 161 | 161 | 0 | 5 | 0.35
20 | 161 | 161 | 0 | 5 | 0.01
21 | 161 | 161 | 0 | 5 | 0.09
22 | 161 | 161 | 0 | 5 | 0.24
23 | 161 | 161 | 0 | 5 | 0.031
24 | 161 | 161 | 0 | 5 | 0.57
25 | 161 | 161 | 0 | 5 | 0.45
26 | 161 | 161 | 0 | 5 | 0.12
27 | 161 | 161 | 0 | 5 | 0.24
28 | 161 | 161 | 0 | 5 | 0.33
29 |  |  |  | 5
30 |  |  |  | 5
31 |  |  |  | 5
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Phillip Merrill
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Phillip Merrill |  | 2025-03-07
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 503) 734.7400 |  | CERT #:T08670
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :B
System Name: | USFS Timberline Lodge 1 |  | ID#: 41 92641 |  | Month/Year: May 2021 |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.8 | 1476.537 | 2657.7665 | 4.7 | 8.1 | 44.9973 | YES | 14.4
2 | 1.6 | 1151.969 | 1843.1504 | 4.3 | 8 | 43.535 | YES | 18.5
3 | 1.7 | 1177.1612 | 2001.174 | 4.7 | 8.1 | 44.4647 | YES | 18.1
4 | 1.7 | 945.1647 | 1606.7799 | 4.7 | 8.1 | 44.4647 | YES | 22.6
5 | 1.7 | 1177.1612 | 2001.174 | 4 | 8.1 | 46.6848 | YES | 18.1
6 | 1.8 | 1245.2979 | 2241.5363 | 4.7 | 8.2 | 46.6982 | YES | 17.1
7 | 1.8 | 1346.7699 | 2424.1858 | 4.4 | 8.1 | 45.9467 | YES | 15.8
8 | 1.8 | 1133.7784 | 2040.8011 | 5.3 | 8.1 | 43.1598 | YES | 18.8
9 | 1.7 | 1151.969 | 1958.3473 | 5.1 | 8.1 | 43.2461 | YES | 18.5
10 | 1.9 | 1050.8901 | 1996.6911 | 5.2 | 7.8 | 39.3696 | YES | 20.3
11 | 1.8 | 1025.9173 | 1846.6512 | 4.6 | 8.3 | 48.8061 | YES | 20.8
12 | 1.6 | 1274.8374 | 2039.7399 | 4.4 | 8.5 | 52.0612 | YES | 16.7
13 | 1.8 | 1740.6296 | 3133.1333 | 4.1 | 8.2 | 48.6941 | YES | 12.2
14 | 1.8 | 966.2765 | 1739.2976 | 4.1 | 8.5 | 54.4593 | YES | 22.1
15 | 1.7 | 1245.2979 | 2117.0065 | 4.2 | 7.9 | 42.7515 | YES | 17.1
16 | 1.9 | 1346.7699 | 2558.8628 | 4.7 | 7.8 | 40.7543 | YES | 15.8
17 | 1.8 | 1121.9704 | 2019.5468 | 4.2 | 7.5 | 37.3338 | YES | 19
18 | 1.7 | 1139.7771 | 1937.621 | 4.1 | 7.6 | 38.5408 | YES | 18.7
19 | 1.5 | 1087.9925 | 1631.9887 | 4 | 7.6 | 37.9018 | YES | 19.6
20 | 1.6 | 1006.7872 | 1610.8596 | 4.5 | 8 | 42.9347 | YES | 21.2
21 | 1.7 | 1390.3891 | 2363.6615 | 4.6 | 8.1 | 44.775 | YES | 15.3
22 | 1.6 | 1390.3891 | 2224.6225 | 4.8 | 8.4 | 48.7734 | YES | 15.3
23 | 1.5 | 1497.1639 | 2245.7459 | 4.7 | 8.7 | 54.2764 | YES | 14.2
24 | 1.5 | 1621.8704 | 2432.8056 | 4.7 | 9.1 | 63.0576 | YES | 13.1
25 | 1.4 | 1170.7593 | 1639.0631 | 4.6 | 9 | 60.4286 | YES | 18.2
26 | 1.4 | 1210.2617 | 1694.3664 | 4.6 | 8.9 | 58.2039 | YES | 17.6
27 | 1.5 | 1099.0849 | 1648.6274 | 4.1 | 9 | 63.3569 | YES | 19.4
28 | 1.5 | 1177.1612 | 1765.7418 | 4.4 | 9 | 62.0304 | YES | 18.1
29 |  | #DIV/0!
30 |  | #DIV/0!
31 |  | #DIV/0!
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2 (CT notes 1563 gallons plug flow up to reservoir, 1892 gallons plug flow down from reservoir, 19197 gallons 10% of min reservoir level)