## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Clackamas
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-04-01
System Name: | USFS Timberline Lodge 1 |  |  | ID#: 41-92641 |  | WTP ID: WTP- B TP for surface water
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 163 | 163 | 0 | 5 | 0.16
2 | 161 | 161 | 0 | 5 | 0.09
3 | 162 | 162 | 0 | 5 | 0.13
4 | 163 | 163 | 0 | 5 | 0.54
5 | 163 | 163 | 0 | 5 | 0.28
6 | 163 | 163 | 0 | 5 | 0.2
7 | 163 | 163 | 0 | 5 | 0.17
8 | 163 | 163 | 0 | 5 | 0.17
9 | 161 | 161 | 0 | 5 | 0.08
10 | 162 | 162 | 0 | 5 | 0.11
11 | 164 | 163 | 1 | 5 | 0.1
12 | 162 | 162 | 0 | 5 | 0.34
13 | 163 | 163 | 0 | 5 | 0.34
14 | 163 | 163 | 0 | 5 | 0.18
15 | 163 | 163 | 0 | 5 | 0.08
16 | 164 | 163 | 1 | 5 | 0.08
17 | 161 | 161 | 0 | 5 | 0.11
18 | 162 | 162 | 0 | 5 | 0.14
19 | 161 | 161 | 0 | 5 | 0.09
20 |  |  |  | 5 |  | switched from surface water
21 |  |  |  | 5 |  | to ground on 5-19-2023
22 |  |  |  | 5
23 |  |  |  | 5
24 |  |  |  | 5
25 |  |  |  | 5
26 |  |  |  | 5 |  | meter malfunctioing
27 |  |  |  | 5 | 0.14
28 |  |  |  | 5 | 0.23
29 |  |  |  | 5 | 0.12
30 |  |  |  | 5 | 0.12
31 |  |  |  | 5
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Phillip Merrill
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Phillip Merrill |  | 2023-06-07
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 503) 734.7400 |  | CERT #:T08670
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :B
System Name: | USFS Timberline Lodge 1 |  | ID#: 41 92641 |  | Month/Year: May 2021 |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.1 | 169.0521 | 185.9573 | 3.4 | 8.2 | 47.0293 | YES | 134.3
2 | 1 | 231.0158 | 231.0158 | 4.2 | 8.1 | 42.3592 | YES | 96.3
3 | 1.1 | 284.8433 | 313.3276 | 4.1 | 8.2 | 44.792 | YES | 77.3
4 | 1 | 269.52 | 269.52 | 4 | 8.1 | 42.951 | YES | 81.9
5 | 1 | 258.678 | 258.678 | 3.7 | 8.1 | 43.8551 | YES | 85.5
6 | 1 | 228.9881 | 228.9881 | 3.9 | 8 | 41.6809 | YES | 97.2
7 | 0.9 | 141.3241 | 127.1917 | 4 | 7.7 | 36.6331 | YES | 163.1
8 | 1.1 | 229.8846 | 252.8731 | 4.35 | 7.7 | 36.6141 | YES | 96.8
9 | 1.2 | 261.302 | 313.5624 | 4 | 7.7 | 37.9519 | YES | 84.6
10 | 1.3 | 229.8846 | 298.85 | 4.1 | 7.5 | 35.4427 | YES | 96.8
11 | 1.1 | 281.7034 | 309.8737 | 4.3 | 7.7 | 36.7402 | YES | 78.2
12 | 1.4 | 240.259 | 336.3626 | 4.4 | 7.7 | 37.8017 | YES | 92.4
13 | 1.2 | 219.1842 | 263.021 | 4.1 | 7.7 | 37.6913 | YES | 101.8
14 | 1.2 | 178.4714 | 214.1657 | 3.9 | 7.7 | 38.2145 | YES | 126.7
15 | 1.2 | 197.0143 | 236.4172 | 4.2 | 7.7 | 37.4326 | YES | 114
16 | 1.1 | 181.0054 | 199.106 | 3.5 | 7.7 | 38.8223 | YES | 124.8
17 | 1.2 | 252.4906 | 302.9887 | 3.7 | 7.6 | 37.3479 | YES | 87.7
18 | 1.2 | 234.0126 | 280.8151 | 3.6 | 7.7 | 39.0137 | YES | 95
19 | 1.2 | 190.5921 | 228.7105 | 3.7 | 7.8 | 40.1982 | YES | 118.1
20 | 1.3 | 212.1085 | 275.741 | 3.5 | 7.8 | 41.2442 | YES | 105.4
21 | 1.2 | 212.1085 | 254.5302 | 3.5 | 7.9 | 42.2909 | YES | 105.4
22 | 1.2 | 185.3098 | 222.3718 | 3.8 | 7.8 | 39.9212 | YES | 121.7
23 | 1.2 | 196.5288 | 235.8345 | 4.2 | 7.8 | 38.8333 | YES | 114.3
24 | 1.4 | 209.6707 | 293.539 | 5.4 | 7.9 | 37.9734 | YES | 106.7
25 | 1.2 | 233.0818 | 279.6981 | 3.9 | 8 | 42.6824 | YES | 95.4
26 | 1.2 | 219.1842 | 263.021 | 3.5 | 8 | 43.8843 | YES | 101.8
27 | 1.2 | 202.357 | 242.8284 | 3.4 | 8 | 44.1904 | YES | 110.8
28 | 1.2 | 200.8234 | 240.9881 | 4.2 | 8 | 41.8038 | YES | 111.7
29 | 1.2 | 192.7343 | 231.2812 | 4.5 | 8 | 40.9441 | YES | 116.7
30 | 1.1 | 213.0622 | 234.3684 | 3.7 | 8.1 | 44.3801 | YES | 104.9
31 | 0.9 | 257.5295 | 231.7765 | 3.6 |  | 3.8967 | YES | 85.9
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2 (CT notes 1563 gallons plug flow up to reservoir, 1892 gallons plug flow down from reservoir, 19197 gallons 10% of min reservoir level)