## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Clackamas
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-04-01
System Name: | USFS Timberline Lodge 1 |  |  | ID#: 41-92641 |  | WTP ID: WTP- B TP for surface water
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 161 | 161 | 0 | 5 | 0.09
2 | 161 | 161 | 0 | 5 | 0.27
3 | 161 | 161 | 0 | 5 | 0.14
4 | 161 | 161 | 0 | 5 | 0.18
5 | 161 | 161 | 0 | 5 | 0.23
6 | 161 | 161 | 0 | 5 | 0.22
7 | 161 | 161 | 0 | 5 | 0.18
8 | 162 | 161 | 1 | 5 | 0.14
9 | 161 | 161 | 0 | 5 | 0.14
10 | 161 | 161 | 0 | 5 | 0.25
11 |  |  |  | 5 |  | no flow
12 | 161 | 161 | 0 | 5 | 0.19
13 | 161 | 161 | 0 | 5 | 0.22
14 | 161 | 161 | 0 | 5 | 0.18
15 | 161 | 161 | 0 | 5 | 0.2
16 | 161 | 161 | 0 | 5 | 0.2
17 | 161 | 161 | 0 | 5 | 0..18
18 | 161 | 161 | 0 | 5 | 0.27
19 | 161 | 161 | 0 | 5 | 0.15
20 | 161 | 161 | 0 | 5 | 0.38
21 | 161 | 161 | 0 | 5 | 0.25
22 | 161 | 161 | 0 | 5 | 0.26
23 | 161 | 161 | 0 | 5 | 0.5
24 | 161 | 161 | 0 | 5 | 0.32
25 | 161 | 161 | 0 | 5 | 0.21
26 | 161 | 161 | 0 | 5 | 0.25
27 | 161 | 161 | 0 | 5 | 0.28
28 | 162 | 161 | 1 | 5 | 0.28
29 | 162 | 162 | 0 | 5 | 0.28
30 | 162 | 162 | 0 | 5 | 0.26
31 |  |  |  | 5
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Phillip Merrill
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Phillip Merrill |  | 2025-05-09
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 503) 734.7400 |  | CERT #:T08670
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :B
System Name: | USFS Timberline Lodge 1 |  | ID#: 41 92641 |  | Month/Year: May 2021 |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.4 | 1245.2979 | 1743.4171 | 3.8 | 7.4 | 35.293 | YES | 17.1
2 | 1.8 | 1006.7872 | 1812.217 | 5 | 8 | 42.468 | YES | 21.2
3 | 1.9 | 1685.7532 | 3202.9311 | 4.8 | 7.6 | 37.6025 | YES | 12.6
4 | 1.5 | 1121.9704 | 1682.9557 | 4 | 7.5 | 36.5366 | YES | 19
5 | 1.7 | 1245.2979 | 2117.0065 | 4.3 | 7.8 | 40.9169 | YES | 17.1
6 | 1.6 | 1170.7593 | 1873.2149 | 4.5 | 7.8 | 39.8796 | YES | 18.2
7 | 1.7 | 997.4904 | 1695.7336 | 4.2 | 7.9 | 42.7515 | YES | 21.4
8 | 1.5 | 776.1173 | 1164.1759 | 4.4 | 8 | 42.723 | YES | 27.6
9 | 1.6 | 1121.9704 | 1795.1527 | 4.5 | 7.4 | 34.4384 | YES | 19
10 | 1.8 | 1346.7699 | 2424.1858 | 4 | 8.2 | 49.0354 | YES | 15.8
11 | 1.9 | 1346.7699 | 2558.8628 | 4.1 | 8 | 45.75 | YES | 15.8
12 | 1.8 | 1390.3891 | 2502.7004 | 4.3 | 7.5 | 37.0777 | YES | 15.3
13 | 1.7 | 1274.8374 | 2167.2237 | 4 | 7.4 | 36.0615 | YES | 16.7
14 | 1.7 | 1099.0849 | 1868.4444 | 4 | 7.4 | 36.0615 | YES | 19.4
15 | 1.7 | 1476.537 | 2510.1128 | 3.9 | 7.3 | 35.0057 | YES | 14.4
16 | 1.4 | 1427.3922 | 1998.3491 | 4.5 | 7.7 | 37.5422 | YES | 14.9
17 | 1.6 | 966.2765 | 1546.0424 | 4.4 | 7.7 | 38.7051 | YES | 22.1
18 | 1.5 | 1151.969 | 1727.9535 | 4.4 | 8 | 42.723 | YES | 18.5
19 | 1.4 | 832.6067 | 1165.6494 | 4.6 | 8 | 41.6374 | YES | 25.7
20 | 1.5 | 1210.2617 | 1815.3926 | 4.1 | 8 | 43.6221 | YES | 17.6
21 | 1.4 | 1099.0849 | 1538.7189 | 4.2 | 8 | 42.8084 | YES | 19.4
22 | 1.6 | 1427.3922 | 2283.8275 | 4.4 | 7.9 | 41.6651 | YES | 14.9
23 | 1.6 | 1177.1612 | 1883.4579 | 4.1 | 7.8 | 40.9985 | YES | 18.1
24 | 1.4 | 1518.3802 | 2125.7323 | 4.2 | 7.6 | 36.9451 | YES | 14
25 | 1.8 | 1427.3922 | 2569.306 | 3.9 | 7.6 | 39.5413 | YES | 14.9
26 | 1.7 | 1456.4751 | 2476.0077 | 3.9 | 7.5 | 37.6664 | YES | 14.6
27 | 1.7 | 1476.537 | 2510.1128 | 4.1 | 7.8 | 41.4875 | YES | 14.4
28 | 1.8 | 1050.8901 | 1891.6021 | 4.7 | 7.4 | 34.7763 | YES | 20.3
29 | 1.5 | 1313.8132 | 1970.7198 | 3.8 | 7.3 | 34.4287 | YES | 16.2
30 | 1.5 | 1313.8132 | 1970.7198 | 3.7 | 7.4 | 35.9564 | YES | 16.2
31 |  | #DIV/0!
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2 (CT notes 1563 gallons plug flow up to reservoir, 1892 gallons plug flow down from reservoir, 19197 gallons 10% of min reservoir level)