## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Marion
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-08-01
System Name: | Whispering Falls |  |  | ID#: 41 | 92786 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 25
2 |  |  |  | 25
3 |  |  |  | 25
4 |  |  |  | 25
5 |  |  |  | 25
6 |  |  |  | 25
7 |  |  |  | 25
8 |  |  |  | 25
9 | 39 | 40 | -1 | 25 | 0.95
10 | 39 | 40 | -1 | 25 | 0.18
11 | 39 | 40 | -1 | 25 | 0.29
12 | 39 | 40 | -1 | 25 | 0.25
13 | 39 | 40 | -1 | 25 | 0.2
14 | 39 | 40 | -1 | 25 | 0.18
15 | 39 | 40 | -1 | 25 | 0.18
16 | 40 | 40 | 0 | 25 | 0.2
17 | 40 | 40 | 0 | 25 | 0.2
18 | 40 | 40 | 0 | 25 | 0.22
19 | 40 | 40 | 0 | 25 | 0.25
20 | 40 | 40 | 0 | 25 | 0.25
21 | 40 | 40 | 0 | 25 | 0.41
22 | 40 | 40 | 0 | 25 | 0.24
23 | 40 | 40 | 0 | 25 | 0.24
24 | 40 | 40 | 0 | 25 | 0.25
25 | 40 | 40 | 0 | 25 | 0.24
26 | 40 | 40 | 0 | 25 | 0.14
27 | 40 | 40 | 0 | 25 | 0.19
28 | 40 | 40 | 0 | 25 | 0.19
29 | 40 | 40 | 0 | 25 | 0.19
30 | 40 | 40 | 0 | 25 | 0.19
31 | 40 | 40 | 0 | 25 | 0.19
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Bob Ovendale
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 9/10/21
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 971 )283-1557 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Whispering Falls |  | ID#: 41 | 92786 | Month/Year: | 2020-09-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1
2
3
4
5
6
7
8
9 | 1.08 | 82 | 88.56 | 17.1 | 7.4 | 27.7123 | YES
10 | 0.77 | 82 | 63.14 | 17.2 | 7.4 | 26.5687 | YES
11 | 0.41 | 82 | 33.62 | 17.7 | 7.7 | 27.568 | YES
12 | 0.41 | 82 | 33.62 | 17.6 | 7.7 | 27.7531 | YES
13 | 0.5 | 82 | 41 | 18.6 | 7.8 | 27.2179 | YES
14 | 0.48 | 82 | 39.36 | 18.6 | 7.9 | 28.184 | YES
15 | 0.52 | 82 | 42.64 | 23.6 | 7.9 | 20.2305 | YES
16 | 0.59 | 82 | 48.38 | 20.1 | 7.4 | 21.4153 | YES
17 | 0.62 | 82 | 50.84 | 18.7 | 7.6 | 25.4437 | YES
18 | 0.37 | 82 | 30.34 | 18.6 | 7.8 | 26.8163 | YES
19 | 0.37 | 82 | 30.34 | 18.8 | 7.4 | 22.7919 | YES
20 | 0.91 | 82 | 74.62 | 19.9 | 7.7 | 25.1899 | YES
21 | 1 | 82 | 82 | 18.9 | 7.8 | 28.2455 | YES
22 | 1 | 82 | 82 | 18.1 | 7.8 | 29.7967 | YES
23 | 2 | 82 | 164 | 18.1 | 7.8 | 33.3905 | YES
24 | 2.01 | 82 | 164.82 | 17.7 | 7.8 | 34.3305 | YES
25 | 1.21 | 82 | 99.22 | 17.5 | 7.8 | 31.7649 | YES
26 | 1.62 | 82 | 132.84 | 17.3 | 7.9 | 34.9979 | YES
27 | 1.02 | 82 | 83.64 | 18 | 8 | 32.3769 | YES
28 | 0.91 | 82 | 74.62 | 18 | 8 | 31.9741 | YES
29 | 0.91 | 82 | 74.62 | 18 | 8 | 31.9741 | YES
30 | 0.91 | 82 | 74.62 | 18 | 8 | 31.9741 | YES
31 | 0.81 | 82 | 66.42 | 18 | 8 | 31.6121 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2