## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Marion
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-05-01
System Name: | Whispering Falls |  |  | ID#: 41-92786 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1
2
3
4
5
6
7
8
9
10
11
12 | 10 | 0 | 10 | 25 | 0.65
13 | 10 | 0 | 10 | 25 | 0.4
14 | 10 | 0 | 10 | 25 | 0.35
15 | 10 | 0 | 10 | 25 | 0.35
16 | 10 | 0 | 10 | 25 | 0.33
17 | 10 | 0 | 10 | 25 | 0.87
18 | 10 | 0 | 10 | 25 | 0.25
19 | 10 | 0 | 10 | 25 | 0.26
20 | 10 | 0 | 10 | 25 | 0.26
21 | 10 | 0 | 10 | 25 | 0.25
22 | 10 | 0 | 10 | 25 | 0.24
23 | 10 | 0 | 10 | 25 | 0.25
24 | 10 | 0 | 10 | 25 | 0.25
25 | 10 | 0 | 10 | 25 | 0.35
26 | 10 | 0 | 10 | 25 | 0.37
27 | 10 | 10 | 0 | 25 | 0.49 | change filter
28 | 10 | 0 | 10 | 25 | 0.17
29 | 10 | 0 | 10 | 25 | 0.18
30 | 10 | 0 | 10 | 25 | 0.17
31 | 10 | 0 | 10 | 25 | 0.17
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Bob Ovendale
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 6/3/22
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 971 )283-1557 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Whispering Falls |  | ID#: 41 | 92786 | Month/Year: | 2022-05-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1
2
3
4
5
6
7
8
9
10
11
12 | 8.8 | 82 | 721.6 | 9.4 | 8.4 | 168.2785 | YES
13 | 8.4 | 82 | 688.8 | 9.6 | 4.2 | 34.2536 | YES
14 | 8.5 | 82 | 697 | 9.9 | 7.7 | 120.2639 | YES
15 | 7.9 | 82 | 647.8 | 11.8 | 7.5 | 90.9259 | YES
16 | 7.6 | 82 | 623.2 | 12.1 | 7.3 | 79.8122 | YES
17 | 0.6 | 82 | 49.2 | 10.3 | 7.8 | 47.8798 | YES
18 | 1.4 | 82 | 114.8 | 11.1 | 7.9 | 51.5382 | YES
19 | 1.5 | 82 | 123 | 11.1 | 7.9 | 52.1332 | YES
20 | 1.5 | 82 | 123 | 11.2 | 7.8 | 49.9708 | YES
21 | 1.5 | 82 | 123 | 11.2 | 7.8 | 49.9708 | YES
22 | 1.2 | 82 | 98.4 | 12 | 7.8 | 45.7888 | YES
23 | 1.2 | 82 | 98.4 | 12.2 | 7.8 | 45.1865 | YES
24 | 1.1 | 82 | 90.2 | 11.7 | 7.8 | 46.1812 | YES
25 | 1 | 82 | 82 | 11.9 | 7.7 | 43.5023 | YES
26 | 1.3 | 82 | 106.6 | 13.9 | 8.1 | 45.5246 | YES
27 | 1.3 | 82 | 106.6 | 12 | 8 | 49.7154 | YES
28 | 1.3 | 82 | 106.6 | 12.9 | 7.9 | 45.1921 | YES
29 | 1.3 | 82 | 106.6 | 12.8 | 8 | 47.1944 | YES
30 | 1.3 | 82 | 106.6 | 12.7 | 8.1 | 49.2839 | YES
31 | 1.2 | 82 | 98.4 | 12.8 | 8.1 | 48.4098 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2