## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Marion
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-07-01
System Name: | Whispering Falls |  |  | ID#: 41 | 92786 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 42 | 33 | 9 | 25 | 0.16
2 | 40 | 31 | 9 | 25 | 0.14
3 | 40 | 31 | 9 | 25 | 0.21
4 | 40 | 30 | 10 | 25 | 0.22
5 | 40 | 30 | 10 | 25 | 0.24
6 | 40 | 30 | 10 | 25 | 0.25
7 | 40 | 32 | 8 | 25 | 0.24
8 | 40 | 30 | 10 | 25 | 0.25
9 | 40 | 30 | 10 | 25 | 0.26
10 | 10 | 0 | 10 | 25 | 0.27
11 | 10 | 0 | 10 | 25 | 0.29
12 | 10 | 0 | 10 | 25 | 0.3
13 | 10 | 0 | 10 | 25 | 0.31
14 | 10 | 0 | 10 | 25 | 0.32
15 | 10 | 0 | 10 | 25 | 0.25
16 | 10 | 0 | 10 | 25 | 0.31
17 | 5 | 0 | 5 | 25 | 0.19
18 | 5 | 0 | 5 | 25 | 0.09
19 | 5 | 0 | 5 | 25 | 0.09
20 | 5 | 0 | 5 | 25 | 0.7
21 | 5 | 0 | 5 | 25 | 0.25
22 | 5 | 0 | 5 | 25 | 0.13
23 | 5 | 0 | 5 | 25 | 0.1
24 | 5 | 0 | 5 | 25 | 0.32
25 | 5 | 0 | 5 | 25 | 0.31
26 | 5 | 0 | 5 | 25 | 0.33
27 | 5 | 0 | 5 | 25 | 0.3
28 | 5 | 0 | 5 | 25 | 0.32
29 | 5 | 0 | 5 | 25 | 0.13
30 | 5 | 0 | 5 | 25 | 0.24
31 | 5 | 0 | 5 | 25 | 0.12
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | Yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Bob Ovendale
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 8/3/22
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 971 )283-1557 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Whispering Falls |  | ID#: 41 | 92786 | Month/Year: | 2022-07-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.7 | 82 | 57.4 | 18.1 | 7.4 | 24.8127 | YES
2 | 0.6 | 82 | 49.2 | 17.2 | 7.9 | 31.3727 | YES
3 | 0.7 | 82 | 57.4 | 17.3 | 8 | 32.7098 | YES
4 | 0.7 | 82 | 57.4 | 17.9 | 7.9 | 30.2842 | YES
5 | 0.8 | 82 | 65.6 | 17.5 | 8 | 32.6462 | YES
6 | 0.9 | 82 | 73.8 | 17 | 8.1 | 35.4223 | YES
7 | 0.8 | 82 | 65.6 | 17.8 | 8.2 | 34.457 | YES
8 | 0.9 | 82 | 73.8 | 17.9 | 8.2 | 34.6196 | YES
9 | 0.8 | 82 | 65.6 | 18 | 8.5 | 37.9839 | YES
10 | 0.8 | 82 | 65.6 | 18.1 | 8.8 | 42.1418 | YES
11 | 0.7 | 82 | 57.4 | 18.2 | 8.9 | 42.9439 | YES
12 | 1 | 82 | 82 | 18.3 | 8 | 31.6637 | YES
13 | 1 | 82 | 82 | 18.3 | 8 | 31.6637 | YES
14 | 1 | 82 | 82 | 18.7 | 7.8 | 28.6258 | YES
15 | 1.3 | 82 | 106.6 | 18.5 | 7.9 | 31.1546 | YES
16 | 1 | 82 | 82 | 17.8 | 8 | 32.7367 | YES
17 | 1 | 82 | 82 | 18.1 | 8 | 32.0887 | YES
18 | 1 | 82 | 82 | 18.2 | 7.9 | 30.7164 | YES
19 | 1 | 82 | 82 | 18.1 | 7.9 | 30.922 | YES
20 | 0.59 | 82 | 48.38 | 18.3 | 7.9 | 29.1183 | YES
21 | 0.53 | 82 | 43.46 | 18.6 | 7.8 | 27.3114 | YES
22 | 0.47 | 82 | 38.54 | 19.2 | 7.9 | 27.0438 | YES
23 | 0.47 | 82 | 38.54 | 19.2 | 8.1 | 29.1297 | YES
24 | 0.45 | 82 | 36.9 | 19.4 | 7.8 | 25.6501 | YES
25 | 0.43 | 82 | 35.26 | 19.5 | 7.8 | 25.4203 | YES
26 | 0.42 | 82 | 34.44 | 19.6 | 7.8 | 25.2214 | YES
27 | 0.41 | 82 | 33.62 | 20.1 | 7.9 | 25.2863 | YES
28 | 0.4 | 82 | 32.8 | 20.2 | 7.8 | 24.17 | YES
29 | 0.43 | 82 | 35.26 | 21.7 | 7.9 | 22.7603 | YES
30 | 0.33 | 82 | 27.06 | 22.4 | 7.8 | 20.673 | YES
31 | 0.38 | 82 | 31.16 | 23.1 | 8.1 | 22.1932 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2