## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Marion
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-09-01
System Name: | Whispering Falls |  |  | ID#: 41 | 92786 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 5 | 0 | 5 | 25 | 0.22
2 | 5 | 0 | 5 | 25 | 0.19
3 | 5 | 0 | 5 | 25 | 0.22
4 | 5 | 0 | 5 | 25 | 0.25
5 | 5 | 0 | 5 | 25 | 0.23
6 | 5 | 0 | 5 | 25 | 0.2
7 | 5 | 0 | 5 | 25 | 0.19
8 | 5 | 0 | 5 | 25 | 0.13
9 |  |  |  | 25
10 |  |  |  | 25
11 |  |  |  | 25
12 |  |  |  | 25
13 |  |  |  | 25
14 |  |  |  | 25
15 |  |  |  | 25
16 |  |  |  | 25
17 |  |  |  | 25
18 |  |  |  | 25
19 |  |  |  | 25
20 |  |  |  | 25
21 |  |  |  | 25
22 |  |  |  | 25
23 |  |  |  | 25
24 |  |  |  | 25
25 |  |  |  | 25
26 |  |  |  | 25
27 |  |  |  | 25
28 |  |  |  | 25
29 |  |  |  | 25
30 |  |  |  | 25
31 |  |  |  | 25
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Bob Ovendle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 9/9/22
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 971 )283-1557 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Whispering Falls |  | ID#: 41 | 92786 | Month/Year: | 2022-09-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.33 | 82 | 27.06 | 21.2 | 7.8 | 22.4163 | YES
2 | 0.35 | 82 | 28.7 | 21.1 | 8 | 24.3744 | YES
3 | 0.39 | 82 | 31.98 | 16.4 | 7.8 | 31.1351 | YES
4 | 0.42 | 82 | 34.44 | 16.8 | 7.9 | 31.5671 | YES
5 | 0.33 | 82 | 27.06 | 18.4 | 7.8 | 27.0538 | YES
6 | 0.35 | 82 | 28.7 | 18.1 | 7.8 | 27.6658 | YES
7 | 0.37 | 82 | 30.34 | 17.6 | 7.9 | 29.756 | YES
8 | 0.33 | 82 | 27.06 | 18.1 | 7.7 | 26.595 | YES
9 |  | 82
10 |  | 82
11 |  | 82
12 |  | 82
13 |  | 82
14 |  | 82
15 |  | 82
16 |  | 82
17 |  | 82
18 |  | 82
19 |  | 82
20 |  | 82
21 |  | 82
22 |  | 82
23 |  | 82
24 |  | 82
25 |  | 82
26 |  | 82
27 |  | 82
28 |  | 82
29 |  | 82
30 |  | 82
31 |  | 82
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2