## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Marion
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-05-01
System Name: | Whispering Falls |  |  | ID#: 41 | 92786 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 25
2 |  |  |  | 25
3 |  |  |  | 25
4 |  |  |  | 25
5 |  |  |  | 25
6 |  |  |  | 25
7 |  |  |  | 25
8 |  |  |  | 25
9 |  |  |  | 25
10 |  |  |  | 25
11 |  |  |  | 25
12 |  |  |  | 25
13 |  |  |  | 25
14 |  |  |  | 25
15 |  |  |  | 25
16 |  |  |  | 25
17 |  |  |  | 25
18 |  |  |  | 25
19 | 5 | 0 | 5 | 25 | 0.7
20 | 5 | 0 | 5 | 25 | 0.71
21 | 5 | 0 | 5 | 25 | 0.71
22 | 5 | 0 | 5 | 25 | 0.79
23 | 5 | 0 | 5 | 25 | 0.35
24 | 5 | 0 | 5 | 25 | 0.1
25 | 5 | 0 | 5 | 25 | 0.15
26 | 5 | 0 | 5 | 25 | 0.32
27 | 5 | 0 | 5 | 25 | 0.32
28 | 5 | 0 | 5 | 25 | 0.3
29 | 5 | 0 | 5 | 25 | 0.11
30 | 5 | 0 | 5 | 25 | 0.13
31 | 5 | 0 | 5 |  | 0.13
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Bob Ovendale
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Bob Ovendale |  | DATE: 6/9/23
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 971 )283-1557 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Whispering Falls |  | ID#: 41 | 92786 | Month/Year: | 2023-05-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 |  | 82
2 |  | 82
3 |  | 82
4 |  | 82
5 |  | 82
6 |  | 82
7 |  | 82
8 |  | 82
9 |  | 82
10 |  | 82
11 |  | 82
12 |  | 82
13 |  | 82
14 |  | 82
15 |  | 82
16 |  | 82
17 |  | 82
18 |  | 82
19 | 1.07 | 82 | 87.74 | 15.5 | 7.7 | 34.4206 | YES
20 | 1.07 | 82 | 87.74 | 15.5 | 7.7 | 34.4206 | YES
21 | 1.07 | 82 | 87.74 | 15.7 | 7.9 | 36.5696 | YES
22 | 1.03 | 82 | 84.46 | 15.7 | 8 | 37.7722 | YES
23 | 1 | 82 | 82 | 15.7 | 8.1 | 39.0577 | YES
24 | 1.08 | 82 | 88.56 | 15.6 | 8.1 | 39.6757 | YES
25 | 1.11 | 82 | 91.02 | 15.6 | 8.1 | 39.8108 | YES
26 | 1.17 | 82 | 95.94 | 15.6 | 8.1 | 40.0823 | YES
27 | 1.17 | 82 | 95.94 | 15.5 | 8.2 | 41.8622 | YES
28 | 1.36 | 82 | 111.52 | 15.5 | 8.2 | 42.7718 | YES
29 | 1.36 | 82 | 111.52 | 13.8 | 8.3 | 49.654 | YES
30 | 1.18 | 82 | 96.76 | 14.7 | 8.4 | 47.5597 | YES
31 | 1.15 | 82 | 94.3 | 14.8 | 8.1 | 42.1697 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2