## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Marion
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-06-01
System Name: | Whispering Falls |  |  | ID#: 41 | 92786 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 0.4 | 0 | 0.4 | 25 | 0.17
2 | 0.4 | 0 | 0.4 | 25 | 0.17
3 | 5 | 0 | 5 | 25 | 0.17
4 | 5 | 0 | 5 | 25 | 0.12
5 | 5 | 0 | 5 | 25 | 0.1
6 | 5 | 0 | 5 | 25 | 0.3
7 | 5 | 0 | 5 | 25 | 0.45
8 | 5 | 0 | 5 | 25 | 0.06
9 | 5 | 0 | 5 | 25 | 0.08
10 | 5 | 0 | 5 | 25 | 0.27
11 | 20 | 0 | 20 | 25 | 0.95
12 | 5 | 0 | 5 | 25 | 0.44
13 | 5 | 0 | 5 | 25 | 0.35
14 | 5 | 0 | 5 | 25 | 0.22
15 | 5 | 0 | 5 | 25 | 0.13
16 | 5 | 0 | 5 | 25 | 0.23
17 | 5 | 0 | 5 | 25 | 0.28
18 | 5 | 0 | 5 | 25 | 0.35
19 | 5 | 0 | 5 | 25 | 0.22
20 | 5 | 0 | 5 | 25 | 0.18
21 | 5 | 0 | 5 | 25 | 0.42
22 | 5 | 0 | 5 | 25 | 0.31
23 | 5 | 0 | 5 | 25 | 0.4
24 | 5 | 0 | 5 | 25 | 0.46
25 | 5 | 0 | 5 | 25 | 0.45
26 | 5 | 0 | 5 | 25 | 0.16
27 | 5 | 0 | 5 | 25 | 0.16
28 | 5 | 0 | 5 | 25 | 0.23
29 | 5 | 0 | 5 | 25 | 0.32
30 | 3 | 0 | 3 | 25 | 0.42
31 |  | 0
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Bob Ovendale
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Bob Ovendale |  | DATE: 7/5/23
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 971 )283-1557 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Whispering Falls |  | ID#: 41 | 92786 | Month/Year: | 2023-06-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.91 | 82 | 74.62 | 14.1 | 8.6 | 51.6533 | YES
2 | 0.95 | 82 | 77.9 | 14.1 | 8.7 | 53.8241 | YES
3 | 0.92 | 82 | 75.44 | 13.8 | 8.1 | 43.9003 | YES
4 | 0.85 | 82 | 69.7 | 14.5 | 8.1 | 41.5806 | YES
5 | 0.85 | 82 | 69.7 | 14.7 | 8.3 | 44.1662 | YES
6 | 0.84 | 82 | 68.88 | 17.7 | 8.3 | 36.1558 | YES
7 | 0.8 | 82 | 65.6 | 17.8 | 8.4 | 37.0979 | YES
8 | 0.81 | 82 | 66.42 | 16.2 | 8.1 | 36.9771 | YES
9 | 0.79 | 82 | 64.78 | 16.6 | 8.3 | 38.6764 | YES
10 | 0.85 | 82 | 69.7 | 16.3 | 8 | 35.5621 | YES
11 | 0.99 | 82 | 81.18 | 15.3 | 8 | 38.6132 | YES
12 | 0.67 | 82 | 54.94 | 15.4 | 8.2 | 39.8213 | YES
13 | 0.67 | 82 | 54.94 | 16.2 | 8 | 35.075 | YES
14 | 0.57 | 82 | 46.74 | 16.1 | 8 | 34.9103 | YES
15 | 0.52 | 82 | 42.64 | 15.2 | 8 | 36.853 | YES
16 | 0.5 | 82 | 41 | 14.1 | 8 | 39.5552 | YES
17 | 0.5 | 82 | 41 | 13.8 | 8 | 40.3502 | YES
18 | 0.6 | 82 | 49.2 | 13.3 | 8.1 | 43.7654 | YES
19 | 0.55 | 82 | 45.1 | 12.8 | 8 | 43.3594 | YES
20 | 0.57 | 82 | 46.74 | 12.3 | 8 | 44.8501 | YES
21 | 0.57 | 82 | 46.74 | 12.4 | 8.1 | 46.1539 | YES
22 | 0.55 | 82 | 45.1 | 12.7 | 8 | 43.6475 | YES
23 | 0.53 | 82 | 43.46 | 13.4 | 7.9 | 40.0724 | YES
24 | 0.53 | 82 | 43.46 | 14.2 | 8 | 39.4274 | YES
25 | 0.5 | 82 | 41 | 14.2 | 8 | 39.2937 | YES
26 | 0.67 | 82 | 54.94 | 15.7 | 8 | 36.2606 | YES
27 | 0.67 | 82 | 54.94 | 15.7 | 8 | 36.2606 | YES
28 | 0.47 | 82 | 38.54 | 15.7 | 7.8 | 32.9207 | YES
29 | 0.47 | 82 | 38.54 | 16.1 | 8.1 | 35.8147 | YES
30 | 0.6 | 82 | 49.2 | 12.8 | 8.2 | 46.9311 | YES
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2