## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Marion
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-07-01
System Name: | Whispering Falls |  |  | ID#: 41 | 92786 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 5 | 0 | 5 | 25 | 0.36
2 | 5 | 0 | 5 | 25 | 0.3
3 | 5 | 0 | 5 | 25 | 0.26
4 | 5 | 0 | 5 | 25 | 0.38
5 | 5 | 0 | 5 | 25 | 0.33
6 | 5 | 0 | 5 | 25 | 0.33
7 | 5 | 0 | 5 | 25 | 0.36
8 | 5 | 0 | 5 | 25 | 0.2
9 | 5 | 0 | 5 | 25 | 0.18
10 | 5 | 0 | 5 | 25 | 0.15
11 | 5 | 0 | 5 | 25 | 0.11
12 | 5 | 0 | 5 | 25 | 0.21
13 | 5 | 0 | 5 | 25 | 0.39
14 | 5 | 0 | 5 | 25 | 0.32
15 | 5 | 0 | 5 | 25 | 0.35
16 | 5 | 0 | 5 | 25 | 0.33
17 | 5 | 0 | 5 | 25 | 0.27
18 | 5 | 0 | 5 | 25 | 0.22
19 | 6 | 0 | 6 | 25 | 0.22
20 | 6 | 0 | 6 | 25 | 0.23
21 | 6 | 0 | 6 | 25 | 0.23
22 | 6 | 0 | 6 | 25 | 0.21
23 | 6 | 0 | 6 | 25 | 0.22
24 | 7 | 0 | 7 | 25 | 0.18
25 | 10 | 0 | 10 | 25 | 0.25
26 | 15 | 0 | 15 | 25 | 0.25
27 | 15 | 0 | 15 | 25 | 0.41
28 | 15 | 0 | 15 | 25 | 0.38
29 | 18 | 0 | 18 | 25 | 0.4
30 | 19 | 0 | 19 | 25 | 0.4
31 | 20 | 0 | 20 | 25 | 0.4
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Bob Ovendale
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 971 )283-1557 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Whispering Falls |  | ID#: 41 | 92786 | Month/Year: | 2023-07-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.46 | 82 | 37.72 | 15.3 | 8 | 36.3605 | YES
2 | 0.43 | 82 | 35.26 | 16.1 | 8 | 34.3594 | YES
3 | 0.45 | 82 | 36.9 | 16.3 | 8 | 33.9822 | YES
4 | 0.44 | 82 | 36.08 | 17 | 8 | 32.3975 | YES
5 | 0.42 | 82 | 34.44 | 17.3 | 8.2 | 34.1172 | YES
6 | 0.44 | 82 | 36.08 | 17.8 | 8.2 | 33.0752 | YES
7 | 0.4 | 82 | 32.8 | 18.7 | 8 | 28.7911 | YES
8 | 0.41 | 82 | 33.62 | 18.6 | 8 | 29.0173 | YES
9 | 0.42 | 82 | 34.44 | 18.5 | 8 | 29.2452 | YES
10 | 0.45 | 82 | 36.9 | 18.2 | 8 | 29.9394 | YES
11 | 0.57 | 82 | 46.74 | 17.6 | 8 | 31.5914 | YES
12 | 0.41 | 82 | 33.62 | 17.3 | 8 | 31.6478 | YES
13 | 0.39 | 82 | 31.98 | 17.8 | 8 | 30.54 | YES
14 | 0.41 | 82 | 33.62 | 17.4 | 8 | 31.4375 | YES
15 | 0.42 | 82 | 34.44 | 17.9 | 8 | 30.4408 | YES
16 | 0.44 | 82 | 36.08 | 18.9 | 7.8 | 26.494 | YES
17 | 0.41 | 82 | 33.62 | 19.1 | 8 | 28.0633 | YES
18 | 0.59 | 82 | 48.38 | 18.6 | 7.9 | 28.5402 | YES | 9650
19 | 0.35 | 82 | 28.7 | 19 | 7.9 | 27.0349 | YES | 9651
20 | 0.34 | 82 | 27.88 | 19.4 | 8 | 27.2864 | YES | 9652
21 | 0.38 | 82 | 31.16 | 19.2 | 8 | 27.7808 | YES | 9653
22 | 0.39 | 82 | 31.98 | 19.7 | 8 | 26.8971 | YES | 9654
23 | 0.39 | 82 | 31.98 | 19.6 | 8.1 | 28.1032 | YES | 9656
24 | 0.39 | 82 | 31.98 | 19.7 | 8.1 | 27.9158 | YES | 9656
25 | 0.43 | 82 | 35.26 | 18.8 | 8 | 28.6974 | YES | 9659
26 | 0.42 | 82 | 34.44 | 18.7 | 7.9 | 27.8048 | YES | 9661
27 | 0.4 | 82 | 32.8 | 18.3 | 8.1 | 30.688 | YES | 9662
28 | 0.48 | 82 | 39.36 | 17.8 | 8.1 | 32.019 | YES | 9664
29 | 0.41 | 82 | 33.62 | 18.1 | 8.1 | 31.1357 | YES | 9669
30 | 0.39 | 82 | 31.98 | 18 | 8.1 | 31.2728 | YES | 9670
31 | 0.39 | 82 | 31.98 | 18.1 | 8.1 | 31.0649 | YES | 9673
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2