## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Marion
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-08-01
System Name: | Whispering Falls |  |  | ID#: 41 | 92786 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 5 | 0 | 5 | 25 | 0.14
2 | 5 | 0 | 5 | 25 | 0.4
3 | 5 | 0 | 5 | 25 | 0.37
4 | 5 | 0 | 5 | 25 | 0.3
5 | 5 | 0 | 5 | 25 | 0.31
6 | 5 | 0 | 5 | 25 | 0.33
7 | 5 | 0 | 5 | 25 | 0.39
8 | 5 | 0 | 5 | 25 | 0.41
9 | 5 | 0 | 5 | 25 | 0.42
10 | 5 | 0 | 5 | 25 | 0.26
11 | 5 | 0 | 5 | 25 | 0.24
12 | 5 | 0 | 5 | 25 | 0.21
13 | 5 | 0 | 5 | 25 | 0.12
14 | 5 | 0 | 5 | 25 | 0.16
15 | 10 | 0 | 10 | 25 | 0.15
16 | 10 | 0 | 10 | 25 | 0.13
17 | 10 | 0 | 10 | 25 | 0.32
18 | 15 | 0 | 15 | 25 | 0.2
19 | 15 | 0 | 15 | 25 | 0.32
20 | 15 | 0 | 15 | 25 | 0.28
21 | 16 | 0 | 16 | 25 | 0.2
22 | 17 | 0 | 17 | 25 | 0.21
23 | 17 | 0 | 17 | 25 | 0.21
24 | 17 | 0 | 17 | 25 | 0.21
25 | 5 | 0 | 5 | 25 | 0.21
26 | 5 | 0 | 5 | 25 | 0.2
27 | 5 | 0 | 5 | 25 | 0.2
28 | 5 | 0 | 5 | 25 | 0.2
29 | 5 | 0 | 5 | 25 | 0.19
30 | 5 | 0 | 5 | 25 | 0.19
31 | 5 | 0 | 5 | 25 | 0.17
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Bob Ovendale
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 9/5/23
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 971 )283-1557 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Whispering Falls |  | ID#: 41 | 92786 | Month/Year: | 2023-08-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.73 | 82 | 59.86 | 17.6 | 8.1 | 33.3847 | YES | 9675
2 | 0.65 | 82 | 53.3 | 16.5 | 8 | 34.3038 | YES | 9677
3 | 0.44 | 82 | 36.08 | 17.2 | 8.1 | 33.1737 | YES | 9670
4 | 0.48 | 82 | 39.36 | 17.6 | 8 | 31.2692 | YES | 9681
5 | 0.48 | 82 | 39.36 | 16.6 | 8 | 33.4241 | YES | 9683
6 | 0.47 | 82 | 38.54 | 17.1 | 8 | 32.2924 | YES | 9688
7 | 0.47 | 82 | 38.54 | 15.6 | 8 | 35.6831 | YES | 9701
8 | 0.45 | 82 | 36.9 | 16.5 | 8 | 33.5328 | YES | 9701
9 | 0.51 | 82 | 41.82 | 17.3 | 8 | 32.0102 | YES | 9702
10 | 0.39 | 82 | 31.98 | 17.7 | 8.1 | 31.9046 | YES | 9707
11 | 0.4 | 82 | 32.8 | 17.8 | 8 | 30.5748 | YES | 9709
12 | 0.41 | 82 | 33.62 | 17.8 | 7.9 | 29.4954 | YES | 9710
13 | 0.4 | 82 | 32.8 | 18.4 | 8 | 29.3741 | YES | 9713
14 | 0.38 | 82 | 31.16 | 19.1 | 8 | 27.9673 | YES | 9716
15 | 0.51 | 82 | 41.82 | 20 | 7.8 | 24.8079 | YES | 9717
16 | 0.53 | 82 | 43.46 | 20.2 | 7.8 | 24.5331 | YES | 9720
17 | 0.59 | 82 | 48.38 | 20.6 | 8 | 25.9091 | YES | 9721
18 | 0.62 | 82 | 50.84 | 20 | 7.9 | 26.0762 | YES | 9723
19 | 0.53 | 82 | 43.46 | 19.5 | 8 | 27.6994 | YES | 9728
20 | 0.55 | 82 | 45.1 | 18 | 8 | 30.6896 | YES | 9729
21 | 0.55 | 82 | 45.1 | 18 | 8 | 30.6896 | YES | 9730
22 | 0.55 | 82 | 45.1 | 18.2 | 7.9 | 29.18 | YES | 9731
23 | 0.36 | 82 | 29.52 | 18 | 7.6 | 25.8843 | YES | 9732
24 | 0.36 | 82 | 29.52 | 18 | 7.7 | 26.8658 | YES | 9733
25 | 0.7 | 82 | 57.4 | 17.7 | 7.9 | 30.6912 | YES | 9735
26 | 0.7 | 82 | 57.4 | 17.7 | 7.9 | 30.6912 | YES | 9736
27 | 0.68 | 82 | 55.76 | 17.7 | 7.9 | 30.6213 | YES | 9737
28 | 0.68 | 82 | 55.76 | 17.5 | 7.9 | 31.0327 | YES | 9738
29 | 0.55 | 82 | 45.1 | 17.5 | 7.9 | 30.5764 | YES | 9739
30 | 0.5 | 82 | 41 | 17.1 | 7.9 | 31.225 | YES | 9741
31 | 0.5 | 82 | 41 | 17.1 | 7.9 | 31.225 | YES | 9711
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2