## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Marion
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-09-01
System Name: | Whispering Falls |  |  | ID#: 41 | 92786 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 5 | 0 | 5 | 25 | 0.21
2 | 5 | 0 | 5 | 25 | 0.2
3 | 5 | 0 | 5 | 25 | 0.2
4 | 5 | 0 | 5 | 25 | 0.21
5 | 5 | 0 | 5 | 25 | 0.21
6 | 5 | 0 | 5 | 25 | 0.21
7 | 5 | 0 | 5 | 25 | 0.25
8 | 5 | 0 | 5 | 25 | 0.28
9 | System closed |  | #VALUE! | 25
10 |  |  |  | 25
11 |  |  |  | 25
12 |  |  |  | 25
13 |  |  |  | 25
14 |  |  |  | 25
15 |  |  |  | 25
16 |  |  |  | 25
17 |  |  |  | 25
18 |  |  |  | 25
19 |  |  |  | 25
20 |  |  |  | 25
21 |  |  |  | 25
22 |  |  |  | 25
23 |  |  |  | 25
24 |  |  |  | 25
25 |  |  |  | 25
26 |  |  |  | 25
27 |  |  |  | 25
28 |  |  |  | 25
29 |  |  |  | 25
30 |  |  |  | 25
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Bob Ovendale
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 971 )283-1557 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Whispering Falls |  | ID#: 41 | 92786 | Month/Year: | 2023-09-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.49 | 82 | 40.18 | 15 | 8.1 | 38.6172 | YES
2 | 0.49 | 82 | 40.18 | 15.4 | 8.1 | 37.6051 | YES
3 | 0.5 | 82 | 41 | 15.4 | 8.1 | 37.6478 | YES
4 | 0.58 | 82 | 47.56 | 15.7 | 8.1 | 37.2415 | YES
5 | 0.52 | 82 | 42.64 | 15.7 | 8.1 | 36.9888 | YES
6 | 0.5 | 82 | 41 | 15.6 | 8 | 35.8048 | YES
7 | 0.5 | 82 | 41 | 15.6 | 8 | 35.8048 | YES
8 | 0.45 | 82 | 36.9 | 15.6 | 8 | 35.6021 | YES
9 | System Closed | 82 | #VALUE! |  |  | #VALUE! | #VALUE!
10 |  | 82
11 |  | 82
12 |  | 82
13 |  | 82
14 |  | 82
15 |  | 82
16 |  | 82
17 |  | 82
18 |  | 82
19 |  | 82
20 |  | 82
21 |  | 82
22 |  | 82
23 |  | 82
24 |  | 82
25 |  | 82
26 |  | 82
27 |  | 82
28 |  | 82
29 |  | 82
30 |  | 82
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2