## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-08-01
System Name: | Riverside |  |  | ID#: 41 | 92787 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 12 | 0 | 12 | 25 | 0.21
2 | 12 | 0 | 12 | 25 | 0.3
3 | 12 | 0 | 12 | 25 | 0.35
4 | 12 | 0 | 12 | 25 | 0.39
5 | 12 | 0 | 12 | 25 | 0.3
6 | 12 | 0 | 12 | 25 | 0.25
7 | 12 | 0 | 12 | 25 | 0.2
8 | 12 | 0 | 12 | 25 | 0.3
9 | 12 | 0 | 12 | 25 | 0.39
10 | 12 | 0 | 12 | 25 | 0.23
11 | 12 | 0 | 12 | 25 | 1.16
12 | 12 | 0 | 12 | 25 | 1
13 | 13 | 0 | 13 | 25 | 0.52
14 | 13 | 0 | 13 | 25 | 0.6
15 | 13 | 0 | 13 | 25 | 0.58
16 | 13 | 0 | 13 | 25 | 0.3
17 | 13 | 0 | 13 | 25 | 0.28
18 | 14 | 0 | 14 | 25 | 0.22
19 | 14 | 0 | 14 | 25 | 0.31
20 | 14 | 0 | 14 | 25 | 0.31
21 | 15 | 0 | 15 | 25 | 0.16
22 | 15 | 0 | 15 | 25 | 0.17
23 | 15 | 0 | 15 | 25 | 0.14
24 | 15 | 0 | 15 | 25 | 0.13
25 | 15 | 0 | 15 | 25 | 0.16
26 | 15 | 0 | 15 | 25 | 0.09
27 | 15 | 0 | 15 | 25 | 0.1
28 | 15 | 0 | 15 | 25 | 0.12
29 | 15 | 0 | 15 | 25 | 0.15
30 | 15 | 0 | 15 | 25 | 0.17
31 | 15 | 0 | 15 | 25 | 0.17
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Bob Ovendale
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 9/3/21
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 971 )283-1557 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Riverside |  | ID#: 41 | 92787 | Month/Year: | 2021-08-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.53 | 115 | 60.95 | 15.9 | 7.3 | 27.1711 | YES
2 | 0.53 | 115 | 60.95 | 16 | 7.4 | 28.0119 | YES
3 | 0.5 | 115 | 57.5 | 16.1 | 7.4 | 27.7299 | YES
4 | 0.54 | 115 | 62.1 | 16.2 | 7.5 | 28.7184 | YES
5 | 0.8 | 115 | 92 | 16.2 | 7.3 | 27.4657 | YES
6 | 0.8 | 115 | 92 | 16.2 | 7.3 | 27.4657 | YES
7 | 0.8 | 115 | 92 | 16.2 | 7.3 | 27.4657 | YES
8 | 1 | 115 | 115 | 15.8 | 7.4 | 29.9532 | YES
9 | 1.1 | 115 | 126.5 | 15.6 | 7.4 | 30.7038 | YES
10 | 0.5 | 115 | 57.5 | 16.3 | 7.3 | 26.3622 | YES
11 | 0.53 | 115 | 60.95 | 16 | 7.3 | 26.9898 | YES
12 | 0.68 | 115 | 78.2 | 16.6 | 7.6 | 29.4854 | YES
13 | 1.21 | 115 | 139.15 | 16 | 7.5 | 31.4149 | YES
14 | 0.88 | 115 | 101.2 | 16.1 | 7.2 | 26.8857 | YES
15 | 0.8 | 115 | 92 | 15.6 | 7.1 | 26.5422 | YES
16 | 0.78 | 115 | 89.7 | 15.7 | 7.4 | 29.4068 | YES
17 | 0.77 | 115 | 88.55 | 15.6 | 7.6 | 31.8451 | YES
18 | 0.77 | 115 | 88.55 | 15.7 | 7.5 | 30.483 | YES
19 | 0.76 | 115 | 87.4 | 15.8 | 7.4 | 29.1444 | YES
20 | 0.43 | 115 | 49.45 | 15.2 | 7.2 | 27.1236 | YES
21 | 1.26 | 115 | 144.9 | 15.1 | 7.4 | 32.3285 | YES
22 | 1.25 | 115 | 143.75 | 15.1 | 7.4 | 32.2917 | YES
23 | 0.3 | 115 | 34.5 | 14.4 | 7.4 | 30.3652 | YES
24 | 1.36 | 115 | 156.4 | 14.7 | 7.2 | 31.1853 | YES
25 | 1.17 | 115 | 134.55 | 14.2 | 7.5 | 35.2549 | YES
26 | 1.42 | 115 | 163.3 | 14.2 | 7.5 | 36.2699 | YES
27 | 1.3 | 115 | 149.5 | 14.2 | 7.5 | 35.7792 | YES
28 | 1.3 | 115 | 149.5 | 14.5 | 7.5 | 35.0725 | YES
29 | 1.28 | 115 | 147.2 | 14.6 | 7.6 | 36.0687 | YES
30 | 1.25 | 115 | 143.75 | 14.6 | 7.6 | 35.9461 | YES
31 | 1.24 | 115 | 142.6 | 14.6 | 7.6 | 35.9053 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2