## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-05-01
System Name: | Riverside |  |  | ID#: 41 | 92787 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1
2
3
4
5
6
7
8
9 | 18 | 4 | 14 | 25 | 0.23
10 | 18 | 4 | 14 | 25 | 0.27
11 | 19 | 4 | 15 | 25 | 0.3
12 | 20 | 4 | 16 | 25 | 0.3
13 | 20 | 4 | 16 | 25 | 0.4
14 | 20 | 4 | 16 | 25 | 0.42
15 | 20 | 4 | 16 | 25 | 0.45
16 | 20 | 4 | 16 | 25 | 0.51
17 | 20 | 4 | 16 | 25 | 2.04
18 | 20 | 4 | 16 | 25 | 2.04
19 | 20 | 4 | 16 | 25 | 0.29
20 | 20 | 4 | 16 | 25 | 0.29
21 | 20 | 4 | 16 | 25 | 0.3
22 | 20 | 4 | 16 | 25 | 0.29
23 | 20 | 6 | 14 | 25 | 0.28
24 | 24 | 6 | 18 | 25 | 0.08
25 | 24 | 6 | 18 | 25 | 0.09
26 | 25 | 6 | 19 | 25 | 0.24 | change filter
27 | 15 | 5 | 10 | 25 | 0.19
28 | 15 | 5 | 10 | 25 | 0.12
29 | 15 | 5 | 10 | 25 | 0.17
30 | 15 | 5 | 10 | 25 | 0.17
31 | 15 | 6 | 9 | 25 | 0.18
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Bob Ovendale
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 6/3/22
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 971 )283-1557 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: |  |  | ID#: 41 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1
2
3
4
5
6
7
8
9 | 0.7 | 115 | 80.5 | 5.1 | 1.3 | 9.3913 | YES
10 | 0.7 | 115 | 80.5 | 5.5 | 7.9 | 69.4612 | YES
11 | 0.7 | 115 | 80.5 | 5.8 | 7.9 | 68.0483 | YES
12 | 0.8 | 115 | 92 | 5.8 | 7.9 | 68.8509 | YES
13 | 0.9 | 115 | 103.5 | 5.9 | 7.9 | 69.1878 | YES
14 | 0.7 | 115 | 80.5 | 6 | 7.8 | 64.7242 | YES
15 | 0.7 | 115 | 80.5 | 6.5 | 7.7 | 60.3312 | YES
16 | 0.6 | 115 | 69 | 7.2 | 7.6 | 54.8665 | YES
17 | 0.6 | 115 | 69 | 7.2 | 7.6 | 54.8665 | YES
18 | 2.9 | 115 | 333.5 | 8.1 | 8.1 | 81.008 | YES
19 | 1.1 | 115 | 126.5 | 8.1 | 8.1 | 65.5401 | YES
20 | 1.1 | 115 | 126.5 | 7.3 | 8.3 | 74.4848 | YES
21 | 1.1 | 115 | 126.5 | 7.4 | 8.1 | 68.7541 | YES
22 | 1 | 115 | 115 | 7.3 | 8 | 65.9708 | YES
23 | 1 | 115 | 115 | 7.3 | 8 | 65.9708 | YES
24 | 0.6 | 115 | 69 | 8.1 | 8.2 | 64.1103 | YES
25 | 0.6 | 115 | 69 | 8.1 | 8.2 | 64.1103 | YES
26 | 0.8 | 115 | 92 | 9.5 | 7.9 | 53.5573 | YES
27 | 0.9 | 115 | 103.5 | 8.7 | 7.9 | 57.181 | YES
28 | 1 | 115 | 115 | 7.4 | 7.9 | 63.1836 | YES
29 | 1 | 115 | 115 | 7.4 | 7.8 | 60.9346 | YES
30 | 1.1 | 115 | 126.5 | 7.5 | 7.7 | 59.0558 | YES
31 | 1.1 | 115 | 126.5 | 7.6 | 7.8 | 60.8157 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2