## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-07-01
System Name: | Riverside |  |  | ID#: 41 | 92787 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 18 | 4 | 14 | 25 | 0.15
2 | 15 | 2 | 13 | 25 | 0.14
3 | 15 | 3 | 12 | 25 | 0.09
4 | 15 | 4 | 11 | 25 | 0.08
5 | 15 | 5 | 10 | 25 | 0.08
6 | 16 | 5 | 11 | 25 | 0.07
7 | 16 | 5 | 11 | 25 | 0.07
8 | 15 | 3 | 12 | 25 | 0.18
9 | 15 | 3 | 12 | 25 | 0.2
10 | 15 | 2 | 13 | 25 | 0.24
11 | 15 | 2 | 13 | 25 | 0.24
12 | 15 | 2 | 13 | 25 | 0.17
13 | 15 | 2 | 13 | 25 | 0.17
14 | 15 | 2 | 13 | 25 | 0.17
15 | 10 | 0 | 10 | 25 | 0.35
16 | 10 | 0 | 10 | 25 | 0.4
17 | 10 | 0 | 10 | 25 | 0.42
18 | 10 | 0 | 10 | 25 | 0.45
19 | 10 | 0 | 10 | 25 | 0.4
20 | 10 | 0 | 10 | 25 | 0.26
21 | 11 | 0 | 11 | 25 | 0.22
22 | 13 | 0 | 13 | 25 | 0.14
23 | 13 | 0 | 13 | 25 | 0.16
24 | 14 | 0 | 14 | 25 | 0.2
25 | 15 | 0 | 15 | 25 | 0.21
26 | 15 | 0 | 15 | 25 | 0.35
27 | 15 | 0 | 15 | 25 | 0.34
28 | 15 | 0 | 15 | 25 | 0.33
29 | 15 | 0 | 15 | 25 | 0.4
30 | 15 | 0 | 15 | 25 | 0.19
31 | 16 | 0 | 16 | 25 | 0.34
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | Yes / No | yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Bob Ovendale
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 8/4/22
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 971 )283-1557 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: |  |  | ID#: 41 |  | Month/Year: | 2022-07-22 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.7 | 115 | 80.5 | 10.8 | 7.7 | 45.2193 | YES
2 | 0.7 | 115 | 80.5 | 11.2 | 7.8 | 45.6187 | YES
3 | 0.9 | 115 | 103.5 | 11.4 | 8 | 49.4343 | YES
4 | 0.8 | 115 | 92 | 11 | 7.9 | 48.442 | YES
5 | 1 | 115 | 115 | 11.5 | 7.5 | 41.6397 | YES
6 | 0.9 | 115 | 103.5 | 11.8 | 7.8 | 44.8481 | YES
7 | 0.8 | 115 | 92 | 12.1 | 7.6 | 40.5379 | YES
8 | 0.8 | 115 | 92 | 11.2 | 7.7 | 44.5406 | YES
9 | 0.9 | 115 | 103.5 | 11.9 | 7.8 | 44.5527 | YES
10 | 0.8 | 115 | 92 | 11.5 | 7.7 | 43.6676 | YES
11 | 0.9 | 115 | 103.5 | 11.8 | 7.8 | 44.8481 | YES
12 | 0.9 | 115 | 103.5 | 12.5 | 8.1 | 47.7352 | YES
13 | 0.9 | 115 | 103.5 | 12.7 | 7.9 | 43.7699 | YES
14 | 0.9 | 115 | 103.5 | 13.1 | 7.6 | 38.1667 | YES
15 | 1.4 | 115 | 161 | 13.3 | 7.9 | 44.5117 | YES
16 | 1.3 | 115 | 149.5 | 13.1 | 7.8 | 42.9877 | YES
17 | 0.9 | 115 | 103.5 | 13.1 | 7.7 | 39.5997 | YES
18 | 0.9 | 115 | 103.5 | 13.2 | 7.7 | 39.3378 | YES
19 | 0.8 | 115 | 92 | 13.2 | 7.7 | 38.8946 | YES
20 | 0.38 | 115 | 43.7 | 12.9 | 7.6 | 36.4618 | YES
21 | 0.45 | 115 | 51.75 | 13.9 | 7.6 | 34.3882 | YES
22 | 0.48 | 115 | 55.2 | 13.7 | 7.7 | 36.2832 | YES
23 | 0.48 | 115 | 55.2 | 14.1 | 7.6 | 34.0494 | YES
24 | 0.47 | 115 | 54.05 | 14.3 | 7.6 | 33.5609 | YES
25 | 0.48 | 115 | 55.2 | 14.4 | 7.6 | 33.3762 | YES
26 | 0.48 | 115 | 55.2 | 14.6 | 7.6 | 32.9345 | YES
27 | 0.45 | 115 | 51.75 | 15.1 | 7.7 | 32.9436 | YES
28 | 0.45 | 115 | 51.75 | 15.1 | 7.6 | 31.7466 | YES
29 | 0.5 | 115 | 57.5 | 15.5 | 7.7 | 32.2603 | YES
30 | 0.42 | 115 | 48.3 | 15.7 | 7.9 | 33.9673 | YES
31 | 0.43 | 115 | 49.45 | 16.6 | 7.9 | 32.0272 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2