## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-06-01
System Name: | Riverside |  |  | ID#: 41 | 92787 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1
2
3
4
5
6
7 | 5 | 0 | 5 | 25 | 0.33
8 | 5 | 0 | 5 | 25 | 0.39
9 | 5 | 0 | 5 | 25 | 0.27
10 | 5 | 0 | 5 | 25 | 0.38
11 | 5 | 0 | 5 | 25 | 0.39
12 | 5 | 0 | 5 | 25 | 0.54
13 | 5 | 0 | 5 | 25 | 0.4
14 | 5 | 0 | 5 | 25 | 0.42
15 | 5 | 0 | 5 | 25 | 0.4
16 | 5 | 0 | 5 | 25 | 0.42
17 | 5 | 0 | 5 | 25 | 0.46
18 | 5 | 0 | 5 | 25 | 0.42
19 | 5 | 0 | 5 | 25 | 0.42
20 | 5 | 0 | 5 | 25 | 0.42
21 | 5 | 0 | 5 | 25 | 0.38
22 | 5 | 0 | 5 | 25 | 0.28
23 | 5 | 0 | 5 | 25 | 0.42
24 | 5 | 0 | 5 | 25 | 0.35
25 | 9 | 0 | 9 | 25 | 0.35
26 | 9 | 0 | 9 | 25 | 0.35
27 | 10 | 0 | 10 | 25 | 0.37
28 | 10 | 0 | 10 | 25 | 0.27
29 | 10 | 0 | 10 | 25 | 0.1
30 | 10 | 0 | 10 | 25 | 0.33
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Bob Ovendale
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 971 )283-1557 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Riverside |  | ID#: 41 | 92787 | Month/Year: | 2023-06-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1
2
3
4
5
6
7 | 0.53 | 116 | 61.48 | 12.1 | 8 | 45.2418 | YES
8 | 0.44 | 115 | 50.6 | 11.5 | 8 | 46.5985 | YES
9 | 0.49 | 115 | 56.35 | 11.9 | 8.3 | 50.7619 | YES
10 | 0.48 | 115 | 55.2 | 11.7 | 8.2 | 49.5882 | YES
11 | 0.49 | 115 | 56.35 | 11.3 | 8.1 | 49.2066 | YES
12 | 0.42 | 115 | 48.3 | 11.8 | 8 | 45.5774 | YES
13 | 0.46 | 115 | 52.9 | 12.1 | 8.1 | 46.4969 | YES
14 | 0.47 | 115 | 54.05 | 12.1 | 8.1 | 46.5498 | YES
15 | 0.37 | 115 | 42.55 | 11.7 | 7.7 | 41.0626 | YES
16 | 0.39 | 115 | 44.85 | 11.3 | 7.8 | 43.7564 | YES
17 | 0.4 | 115 | 46 | 10.7 | 7.8 | 45.5774 | YES
18 | 0.42 | 115 | 48.3 | 10.7 | 7.9 | 47.3247 | YES
19 | 0.5 | 115 | 57.5 | 10.1 | 8.1 | 53.385 | YES
20 | 0.5 | 115 | 57.5 | 9.6 | 8.1 | 55.212 | YES
21 | 0.48 | 115 | 55.2 | 9.6 | 7.8 | 49.4841 | YES
22 | 0.48 | 115 | 55.2 | 9.4 | 8 | 53.864 | YES
23 | 0.43 | 115 | 49.45 | 9.9 | 7.6 | 44.9355 | YES
24 | 0.43 | 115 | 49.45 | 11.1 | 7.9 | 46.1372 | YES
25 | 0.4 | 115 | 46 | 10.7 | 7.8 | 45.5774 | YES
26 | 0.4 | 115 | 46 | 10.8 | 7.8 | 45.2767 | YES
27 | 0.68 | 115 | 78.2 | 10.8 | 7.8 | 46.7385 | YES
28 | 0.39 | 115 | 44.85 | 11.3 | 7.7 | 42.2486 | YES
29 | 0.41 | 115 | 47.15 | 11.6 | 7.8 | 42.9971 | YES
30 | 0.45 | 115 | 51.75 | 13.1 | 7.9 | 40.509 | YES
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2