## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-07-01
System Name: | Riverside |  |  | ID#: 41 | 92787 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 9 | 0 | 9 | 25 | 0.51
2 | 9 | 0 | 9 | 25 | 0.3
3 | 9 | 0 | 9 | 25 | 0.28
4 | 9 | 0 | 9 | 25 | 0.15
5 | 9 | 0 | 9 | 25 | 0.27
6 | 9 | 0 | 9 | 25 | 0.43
7 | 9 | 0 | 9 | 25 | 0.35
8 | 9 | 0 | 9 | 25 | 0.34
9 | 9 | 0 | 9 | 25 | 0.31
10 | 10 | 0 | 10 | 25 | 0.29
11 | 10 | 0 | 10 | 25 | 0.2
12 | 10 | 0 | 10 | 25 | 0.26
13 | 10 | 0 | 10 | 25 | 0.6
14 | 10 | 0 | 10 | 25 | 0.23
15 | 11 | 0 | 11 | 25 | 0.24
16 | 11 | 0 | 11 | 25 | 0.24
17 | 11 | 0 | 11 | 25 | 0.29
18 | 11 | 0 | 11 | 25 | 0.28
19 | 11 | 0 | 11 | 25 | 0.29
20 | 11 | 0 | 11 | 25 | 0.21
21 | 11 | 0 | 11 | 25 | 0.31
22 | 11 | 0 | 11 | 25 | 0.31
23 | 12 | 0 | 12 | 25 | 0.32
24 | 12 | 0 | 12 | 25 | 0.33
25 | 15 | 0 | 15 | 25 | 0.17
26 | 15 | 0 | 15 | 25 | 0.24
27 | 15 | 0 | 15 | 25 | 0.17
28 | 20 | 0 | 20 | 25 | 0.09
29 | 25 | 0 | 25 | 25 | 0.43
30 | 25 | 0 | 25 | 25 | 0.44
31 | 30 | 0 | 30 | 25 | 0.54
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Bob Ovendale
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 971 )283-1557 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Riverside |  | ID#: 41 | 92787 | Month/Year: | 2023-07-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.5 | 82 | 41 | 13.2 | 7.8 | 39.0059 | YES
2 | 0.5 | 82 | 41 | 12.7 | 7.7 | 38.8628 | YES
3 | 0.5 | 82 | 41 | 12.8 | 7.7 | 38.6057 | YES
4 | 0.52 | 82 | 42.64 | 12.9 | 7.9 | 41.3763 | YES
5 | 0.51 | 82 | 41.82 | 13.1 | 7.8 | 39.3101 | YES
6 | 0.52 | 82 | 42.64 | 13.3 | 8 | 41.8046 | YES
7 | 0.43 | 82 | 35.26 | 14.1 | 7.7 | 35.131 | YES
8 | 0.5 | 82 | 41 | 14.2 | 7.7 | 35.1767 | YES
9 | 0.55 | 82 | 45.1 | 14 | 7.7 | 35.8506 | YES
10 | 0.54 | 82 | 44.28 | 13.8 | 7.7 | 36.2892 | YES
11 | 0.55 | 82 | 45.1 | 13.6 | 7.7 | 36.8165 | YES
12 | 0.51 | 82 | 41.82 | 13.6 | 7.8 | 38.027 | YES
13 | 0.55 | 82 | 45.1 | 14.1 | 8 | 39.7799 | YES
14 | 0.5 | 82 | 41 | 14.2 | 8.1 | 40.7681 | YES
15 | 0.48 | 82 | 39.36 | 14.3 | 8 | 38.9454 | YES
16 | 0.44 | 82 | 36.08 | 14.6 | 7.6 | 32.785 | YES
17 | 0.41 | 82 | 33.62 | 14.3 | 7.6 | 33.3328 | YES
18 | 0.5 | 82 | 41 | 14.2 | 7.8 | 36.4998 | YES
19 | 0.5 | 82 | 41 | 14.5 | 7.7 | 34.4817 | YES | 67369
20 | 0.51 | 82 | 41.82 | 15.1 | 7.9 | 35.7137 | YES | 37390
21 | 0.46 | 82 | 37.72 | 14.6 | 7.7 | 34.0976 | YES | 67407
22 | 0.49 | 82 | 40.18 | 14.6 | 7.6 | 32.972 | YES | 67423
23 | 0.49 | 82 | 40.18 | 14.7 | 7.6 | 32.7531 | YES | 67453
24 | 0.5 | 82 | 41 | 14.8 | 7.6 | 32.5727 | YES | 67457
25 | 0.5 | 82 | 41 | 14 | 7.8 | 36.9881 | YES | 67475
26 | 0.44 | 82 | 36.08 | 14.7 | 7.6 | 32.5673 | YES | 67495
27 | 0.44 | 82 | 36.08 | 14.8 | 7.8 | 34.8343 | YES | 67514
28 | 0.44 | 82 | 36.08 | 14.2 | 7.7 | 34.9378 | YES | 67533
29 | 0.49 | 82 | 40.18 | 14.2 | 7.7 | 35.1368 | YES | 67550
30 | 0.5 | 82 | 41 | 14.3 | 7.7 | 34.9435 | YES | 67571
31 | 0.51 | 82 | 41.82 | 14.7 | 7.7 | 34.0644 | YES | 67585
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2