## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-08-01
System Name: | Riverside |  |  | ID#: 41 | 92787 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 8 | 0 | 8 | 25 | 0.19
2 | 8 | 0 | 8 | 25 | 0.28
3 | 8 | 0 | 8 | 25 | 0.23
4 | 8 | 0 | 8 | 25 | 0.42
5 | 8 | 0 | 8 | 25 | 0.4
6 | 8 | 0 | 8 | 25 | 0.28
7 | 8 | 0 | 8 | 25 | 0.16
8 | 8 | 0 | 8 | 25 | 0.16
9 | 8 | 0 | 8 | 25 | 0.17
10 | 8 | 0 | 8 | 25 | 0.29
11 | 8 | 0 | 8 | 25 | 0.21
12 | 8 | 0 | 8 | 25 | 0.15
13 | 8 | 0 | 8 | 25 | 0.21
14 | 8 | 0 | 8 | 25 | 0.28
15 | 8 | 0 | 8 | 25 | 0.28
16 | 8 | 0 | 8 | 25 | 0.28
17 | 8 | 0 | 8 | 25 | 0.26
18 | 9 | 0 | 9 | 25 | 0.23
19 | 9 | 0 | 9 | 25 | 0.23
20 | 8 | 0 | 8 | 25 | 0.25
21 | 8 | 0 | 8 | 25 | 0.2
22 | 8 | 0 | 8 | 25 | 0.17
23 | 8 | 0 | 8 | 25 | 0.19
24 | 8 | 0 | 8 | 25 | 0.21
25 | 8 | 0 | 8 | 25 | 0.23
26 | 10 | 0 | 10 | 25 | 0.22
27 | 11 | 0 | 11 | 25 | 0.22
28 | 11 | 0 | 11 | 25 | 0.21
29 | 13 | 0 | 13 | 25 | 0.21
30 | 15 | 0 | 15 | 25 | 0.21
31 | 15 | 0 | 15 | 25 | 0.21
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Bob Ovendale
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 971 )283-1557 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Riverside |  | ID#: 41 | 92787 | Month/Year: | 2023-08-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.41 | 115 | 47.15 | 13.7 | 7.7 | 35.9961 | YES | 67602
2 | 0.45 | 115 | 51.75 | 14.2 | 7.8 | 36.2933 | YES | 67620
3 | 0.42 | 115 | 48.3 | 14.2 | 7.8 | 36.1699 | YES | 67640
4 | 0.44 | 115 | 50.6 | 14.2 | 7.7 | 34.9378 | YES | 67654
5 | 0.37 | 115 | 42.55 | 14.2 | 7.8 | 35.9652 | YES | 67673
6 | 0.41 | 115 | 47.15 | 14.2 | 7.8 | 36.1289 | YES | 67689
7 | 0.42 | 115 | 48.3 | 14.2 | 7.6 | 33.5936 | YES | 67707
8 | 0.38 | 115 | 43.7 | 14.2 | 7.5 | 32.2265 | YES | 67725
9 | 0.34 | 115 | 39.1 | 14.2 | 7.5 | 32.0802 | YES | 67740
10 | 0.5 | 115 | 57.5 | 14.4 | 7.8 | 36.0178 | YES | 67759
11 | 0.59 | 115 | 67.85 | 14.2 | 7.8 | 36.8745 | YES | 67763
12 | 0.6 | 115 | 69 | 14.2 | 7.7 | 35.5785 | YES | 67791
13 | 0.58 | 115 | 66.7 | 14.8 | 7.7 | 34.1088 | YES | 67802
14 | 0.58 | 115 | 66.7 | 15.1 | 7.6 | 32.2199 | YES | 67825
15 | 0.55 | 115 | 63.25 | 15.4 | 7.6 | 31.4743 | YES | 67842
16 | 0.55 | 115 | 63.25 | 15.7 | 7.6 | 30.8507 | YES | 67861
17 | 0.58 | 115 | 66.7 | 15.9 | 7.8 | 32.8941 | YES | 67876
18 | 0.36 | 115 | 41.4 | 16.3 | 7.5 | 27.9466 | YES | 67896
19 | 0.59 | 115 | 67.85 | 16 | 7.7 | 31.524 | YES | 67913
20 | 0.54 | 115 | 62.1 | 15.7 | 7.6 | 30.8156 | YES | 67949
21 | 0.45 | 115 | 51.75 | 15.4 | 7.4 | 28.8935 | YES | 67951
22 | 0.45 | 115 | 51.75 | 15.1 | 7.2 | 27.3683 | YES | 67957
23 | 0.48 | 115 | 55.2 | 14.7 | 7.7 | 33.9485 | YES | 67999
24 | 0.48 | 115 | 55.2 | 14.6 | 7.7 | 34.1752 | YES | 68990
25 | 0.48 | 115 | 55.2 | 14.7 | 7.7 | 33.9485 | YES | 68009
26 | 0.48 | 115 | 55.2 | 14.7 | 7.7 | 33.9485 | YES | 68012
27 | 0.49 | 115 | 56.35 | 14.6 | 7.6 | 32.972 | YES | 67030
28 | 0.49 | 115 | 56.35 | 14.6 | 7.6 | 32.972 | YES | 68042
29 | 0.49 | 115 | 56.35 | 14.7 | 7.6 | 32.7531 | YES | 68067
30 | 0.48 | 115 | 55.2 | 14.7 | 7.5 | 31.5269 | YES | 68096
31 | 0.49 | 115 | 56.35 | 14.7 | 7.5 | 31.5629 | YES | 68112
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2