## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-09-01
System Name: | Riverside |  |  | ID#: 41 | 92787 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 15 | 0 | 15 | 25 | 0.26
2 | 15 | 0 | 15 | 25 | 0.26
3 | 16 | 0 | 16 | 25 | 0.26
4 | 20 | 0 | 20 | 25 | 0.26
5 | 20 | 0 | 20 | 25 | 0.27
6 | 20 | 0 | 20 | 25 | 0.27
7 | 20 | 0 | 20 | 25 | 0.27
8 | 20 | 0 | 20 | 25 | 0.27
9 |  |  |  | 25 |  | system closed
10 |  |  |  | 25
11 |  |  |  | 25
12 |  |  |  | 25
13 |  |  |  | 25
14 |  |  |  | 25
15 |  |  |  | 25
16 |  |  |  | 25
17 |  |  |  | 25
18 |  |  |  | 25
19 |  |  |  | 25
20 |  |  |  | 25
21 |  |  |  | 25
22 |  |  |  | 25
23 |  |  |  | 25
24 |  |  |  | 25
25 |  |  |  | 25
26 |  |  |  | 25
27 |  |  |  | 25
28 |  |  |  | 25
29 |  |  |  | 25
30 |  |  |  | 25
31 |  |  |  | 25
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Bob Ovendale
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 971 )283-1557 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Riverside |  | ID#: 41 | 92787 | Month/Year: | 2023-09-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.5 | 115 | 57.5 | 14.3 | 7.6 | 33.6756 | YES
2 | 0.5 | 115 | 57.5 | 14.1 | 7.6 | 34.1269 | YES
3 | 0.5 | 115 | 57.5 | 13.9 | 7.6 | 34.5842 | YES
4 | 0.5 | 115 | 57.5 | 14.1 | 7.6 | 34.1269 | YES | 68180
5 | 0.49 | 115 | 56.35 | 14.1 | 7.6 | 34.0882 | YES
6 | 0.49 | 115 | 56.35 | 14.1 | 7.6 | 34.0882 | YES
7 | 0.49 | 115 | 56.35 | 14.2 | 7.6 | 33.862 | YES | 68298
8 | system closed |  | #VALUE! |  |  | #VALUE! | #VALUE!
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2