## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-06-25
System Name: | USFS Big Lake |  |  | ID#: 41 | 92802 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]Highest Reading of the day 1 [NTU]
1
2
3
4
5
6
7
8
9
10 | 7.5 | 25 | 17.5 | 25 | 0.22
11 | 7.5 | 25 | 17.5 | 25 | 0.23
12 | 7.5 | 30 | 22.5 | 25 | 0.19
13 | 7.5 | 30 | 19.5 | 25 | 0.18
14 | 7.5 | 35 | 5 | 25 | 0.21
15 | 7.5 | 40 | 22.5 | 25 | 0.19
16 | 5 | 0 | 5 | 25 | 0.23
17 | 5 | 5 | 0 | 25 | 0.25
18 | 5 | 5 | 0 | 25 | 0.22
19 | 5 | 10 | 2.5 | 25 | 0.31
20 | 5 | 10 | 2.5 | 25 | 0.28
21 | 7.5 | 15 | 7.5 | 25 | 0.27
22 | 7.5 | 15 | 7.5 | 25 | 0.26
23 | 7.5 | 20 | 12.5 | 25 | 0.29
24 | 7.5 | 20 | 5 | 25 | 0.3
25 | 7.5 | 25 | 12.5 | 25 | 0.28
26 | 7.5 | 25 | 17.5 | 25 | 0.31
27 | 7.5 | 30 | 22.5 | 25 | 0.3
28 | 7.5 | 30 | 21.5 | 25 | 0.26
29 | 7.5 | 30 | 23.5 | 25 | 0.28
30 | 7.5 | 0 | 8.5 | 25 | 0.26
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ? 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ? 0.2 mg/l?
All daily turbidity readings ? 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( ) |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | USFS Big Lake |  | ID#: 41 | 82802 | Month/Year: | 2025-06-25 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2CT Met? 2CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1
2
3
4
5
6
7
8
9
10 / 8 am | 1 | 51 | 51 | 13 | 6.77 | 28.5867 | YES
11 / 9am | 1.1 | 51 | 56.1 | 13 | 6.79 | 29.1303 | YES
12 / 9am | 0.8 | 51 | 40.8 | 13.2 | 6.68 | 26.6622 | YES
13 / 9 am | 0.9 | 51 | 45.9 | 13.2 | 6.63 | 26.4719 | YES
14 / 8 am | 1 | 51 | 51 | 13.3 | 6.6 | 26.3025 | YES
15 / 8 am | 0.9 | 51 | 45.9 | 13 | 6.7 | 27.5365 | YES
16 / 8 am | 0.8 | 51 | 40.8 | 13.2 | 6.57 | 25.5925 | YES
17 / 8 am | 0.8 | 51 | 40.8 | 13.5 | 6.66 | 25.9377 | YES
18 / 9 am | 0.9 | 51 | 45.9 | 13.3 | 6.8 | 28.0111 | YES
19 / 9 am | 0.9 | 51 | 45.9 | 13.4 | 6.75 | 27.312 | YES
20 / 8 am | 1 | 51 | 51 | 13.1 | 6.96 | 30.4702 | YES
21 / 9 am | 0.9 | 51 | 45.9 | 13.5 | 7.23 | 32.4171 | YES
22 / 10 am | 0.8 | 51 | 40.8 | 13.3 | 7.33 | 33.7043 | YES
23 / 8 am | 1 | 51 | 51 | 13.2 | 7.4 | 35.6185 | YES
24 / 8 am | 1.2 | 51 | 61.2 | 13.5 | 7.56 | 37.8893 | YES
25 / 9 am | 1 | 51 | 51 | 13.2 | 7.42 | 35.8825 | YES
26 / 10 am | 0.9 | 51 | 45.9 | 13.3 | 7.98 | 43.321 | YES
27 / 10 am | 0.8 | 51 | 40.8 | 13.2 | 7.79 | 40.206 | YES
28 / 9 am | 0.9 | 51 | 45.9 | 13.5 | 7.5 | 35.8195 | YES
29 / 9 am | 0.9 | 51 | 45.9 | 13.6 | 7.69 | 38.1663 | YES
30 / 9 am | 0.9 | 51 | 45.9 | 13.2 | 7.88 | 42.0337 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2