## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Josephine
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-10-01
System Name: | Black Bar Lodge |  |  | ID#: 41 | 4193465 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.3 |  |  |  | 0.3
2 |  |  | 0.3 |  |  |  | 0.3
3 |  |  | 0.2 |  |  |  | 0.2
4 |  |  | 0.2 |  |  |  | 0.2
5 |  |  | 0.3 |  |  |  | 0.3
6 |  |  | 0.3 |  |  |  | 0.3
7 |  |  | 0.2 |  |  |  | 0.2
8 |  |  | 0.3 |  |  |  | 0.3
9 |  |  | 0.3 |  |  |  | 0.3
10 |  |  | 0.4 |  |  |  | 0.4
11 |  |  | 0.3 |  |  |  | 0.3
12 |  |  | 0.3 |  |  |  | 0.3
13 |  |  | 0.3 |  |  |  | 0.2
14 |  |  | 0.4 |  |  |  | 0.4
15 |  |  | 0.3 |  |  |  | 0.2
16 |  |  | 0.3 |  |  |  | 0.3
17 |  |  | 0.3 |  |  |  | 0.3
18 |  |  | 0.4 |  |  |  | 0.4
19 |  |  | 0.3 |  |  |  | 0.3
20 |  |  | 0.3 |  |  |  | 0.3
21 |  |  | 0.2 |  |  |  | 0.2
22 |  |  | 0.2 |  |  |  | 0.2
23 |  |  | 0.3 |  |  |  | 0.3
24 |  |  | 0.2 |  |  |  | 0.2
25 |  |  | 0.3 |  |  |  | 0.3
26 |  |  | 0.3 |  |  |  | 0.3
27 |  |  | 0.2 |  |  |  | 0.2
28 |  |  | 0.2 |  |  |  | 0.2
29 |  |  | 0.2 |  |  |  | 0.2
30 |  |  | 0.2 |  |  |  | 0.2
31 |  |  | 0.2 |  |  |  | 0.2
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | Printed Name: John M James
[5 empty] | SIGNATURE: |  |  | 2023-11-09
[5 empty] | Phone: # 541-479-6507 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Black Bar Lodge |  | ID#: 41 | 93465 | Month/Year: | 2023-10-23 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.9 | 60 | 54 | 16.1 | 7.98 | 35.9766 | YES | 20
2 | 0.9 | 60 | 54 | 16 | 7.95 | 35.8176 | YES | 20
3 | 0.9 | 60 | 54 | 15.5 | 7.9 | 36.3508 | YES | 20
4 | 0.85 | 60 | 51 | 15.2 | 8 | 38.2584 | YES | 20
5 | 0.9 | 60 | 54 | 15 | 7.98 | 38.7036 | YES | 20
6 | 0.95 | 60 | 57 | 15 | 8 | 39.2115 | YES | 20
7 | 0.95 | 60 | 57 | 14.8 | 7.98 | 39.4435 | YES | 20
8 | 0.95 | 60 | 57 | 14.6 | 7.9 | 38.8093 | YES | 20
9 | 1 | 60 | 60 | 14.2 | 7.95 | 40.8243 | YES | 20
10 | 0.95 | 60 | 57 | 14.2 | 7.98 | 41.0447 | YES | 20
11 | 0.9 | 60 | 54 | 14.2 | 8 | 41.1147 | YES | 20
12 | 0.95 | 60 | 57 | 14.3 | 8 | 41.0748 | YES | 20
13 | 0.95 | 60 | 57 | 14.4 | 7.98 | 40.504 | YES | 20
14 | 0.9 | 60 | 54 | 14.2 | 7.9 | 39.628 | YES | 20
15 | 0.9 | 60 | 54 | 14.2 | 7.95 | 40.3646 | YES | 20
16 | 0.95 | 60 | 57 | 14.3 | 7.98 | 40.7735 | YES | 20
17 | 0.95 | 60 | 57 | 14.4 | 7.99 | 40.6535 | YES | 20
18 | 0.95 | 60 | 57 | 14.2 | 7.98 | 41.0447 | YES | 20
19 | 0.95 | 60 | 57 | 14.1 | 7.98 | 41.3177 | YES | 20
20 | 0.9 | 60 | 54 | 14.1 | 7.95 | 40.6331 | YES | 20
21 | 1 | 60 | 60 | 14 | 7.95 | 41.3691 | YES | 20
22 | 1 | 60 | 60 | 14.1 | 7.95 | 41.0958 | YES | 20
23 | 0.95 | 60 | 57 | 14 | 7.96 | 41.2874 | YES | 20
24 | 0.95 | 60 | 57 | 13.9 | 7.98 | 41.869 | YES | 20
25 | 0.95 | 60 | 57 | 14 | 7.98 | 41.5924 | YES | 20
26 | 0.9 | 60 | 54 | 14.1 | 7.96 | 40.7831 | YES | 20
27 | 0.9 | 60 | 54 | 14.1 | 7.96 | 40.7831 | YES | 20
28 | 0.95 | 60 | 57 | 14.1 | 7.96 | 41.0146 | YES | 20
29 | 0.95 | 60 | 57 | 14 | 7.95 | 41.1356 | YES | 20
30 | 0.95 | 60 | 57 | 13.8 | 7.95 | 41.6846 | YES | 20
31 | 0.9 | 60 | 54 | 13.8 | 7.95 | 41.4493 | YES | 20
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2